## Interface parameters
№ п/п | Тип интерфейса Interface type | Тип протокола Protocol type | Slave станция (Источник данных) Slave Station (Data Source) | Slave ID основной Slave ID main | Slave ID резервный Slave ID back-up | Скорость speed | Бит четности Parity bit | Стоп бит Stop bit | Бит данных Data bit | Реверс reverse | Таймаут timeout | максимальная длина maximum length | Примечание note
1 | TCP/IP | Modbus TCP | IMCS EBSM102 | 192.168.4.10(Default) 255.255.255.0 port 502 | 192.168.5.10(Default) 255.255.255.0 port 502 | 100Mbps | none | 1 | 8 | N | 100ms | 100
2 | TCP/IP | Modbus TCP | IMCS EBSM102 | 192.168.4.11(Default) 255.255.255.0 port 502 | 192.168.5.11(Default) 255.255.255.0 port 502 | 100Mbps | none | 1 | 8 | N | 100ms | 100
Столбец 1: Column 1:
Указывается порядковый номер интерфейса Specifies the serial number of the interface
Столбец 2: Column 2:
Указывается тип интерфейса: Specifies the type of interface:
ТСР/IP
или последовательные интерфейсы: or serial interfaces:
RS-485 2-Wire
RS-485 4-Wire
RS-422
Столбец 3: Column 3:
Указывается тип протокола обмена информацией: Specify the type of communication protocol:
OPC
Modbus TCP
Modbus RTU
Modbus ASCII
МЭК 60870-5-103
МЭК 60870-5-104
МЭК 61850-8-1
Столбец 4: Column 4:
Указывается функциональное обозначение позиции ПЛК по проекту Project PLC Item Functional Designation to be specified
Столбец 5: Column 5:
Указывается цифровое значени уникальный адрес устройства, для ТСР/IP = адрес ХХХ.ХХХ.ХХХ.ХХХ / маска сети ХХХ.ХХХ.ХХХ.ХХХ / порт XXX или MB = 0..247 Specify the digital value of the unique device address, for TCP/IP = ХХХ.ХХХ.ХХ.ХХ/network mask ХХХ.ХХ.ХХ.ХХ/port XXX or MB = 0.. 247
Столбец 6: Column 6:
Указывается цифровое значени уникальный адрес резервного устройства, для ТСР/IP = адрес ХХХ.ХХХ.ХХХ.ХХХ / маска сети ХХХ.ХХХ.ХХХ.ХХХ / порт XXX или MB = 0..247 Specify the digital value of the unique address of the standby device, for TCP/IP = address ХХХ.ХХХ.ХХ.ХХ/network mask ХХХ.ХХХ.ХХ/port XXX or MB = 0.. 247
Столбец 7: Column 7:
Заполняется для последовательных интерфейсов значение скорости обмена информацией: 115200, 38400, 19200, 9600, 4800 The communication rate value for serial interfaces is 115200, 38400, 19200, 9600, 4800.
Столбец 8: Column 8:
Заполняется для последовательных интерфейсов режим контроля четности: нет, четный, нечетный Parity check mode is filled for serial interfaces: none, even, odd
Столбец 9: Column 9:
Заполняется для последовательных интерфейсов количество стоповых битов, 1 или 2 Number of stop bits, 1 or 2 is filled for serial interfaces
Столбец 10: Column 10:
Заполняется для последовательных интерфейсов число информационных бит в передаваемых и принимаемых байтах, 7 или 8 The number of information bits in transmitted and received bytes is filled for serial interfaces, 7 or 8
Столбец 11: Column 11:
N - стандартный порядок битов, байтов N is the standard order of bits, bytes
RB - инвертированный порядок байт в регистре, сначала младший байт, затем старший RB - inverted byte order in the register, first the lowest byte, then the highest
RR - инвертированный порядок регистров RR - inverted register order
Столбец 12: Column 12:
Указывается максимальное время ожидания ответа устройства на шине, мс Specifies the maximum time to wait for a device response on the bus, ms
Столбец 13: Column 13:
Указывается максимальное количество регистров, которые можно получить в одном запросе Specifies the maximum number of registers that can be obtained in a single request
Столбец 14: Column 14:
Дополнительная информация. Additional information.

## Register Table Function 02
№ п/п | Функциональное обозначение по проекту Project Functional Designation | Tег ПЛК / Hаименование переменной PLC Tag/Variable Name | Описание переменной Description of the variable | Единицы измерения Units of measurement | Шкала scale | LL | LA | HA | HH | Коэффициенты масштабирования Scaling factors | Тип сигнала (Импульс/Постоянный ) Signal type (Impulse/Permanent) | Тип регистра Register type | Адрес/бит Address/Bit | Тип доступа Access type | Тип данных Data type | Код функции Function code | Канал РСУ DCS channel | Tег РСУ / Hаименование переменной DCS Tag/Name variable | Функции РСУ DCS functions | Примечание note
1 | 2202-NK-SG-102-A.03OC_1 | 1115-PM-101A_TX.MCU | MCU.1115-PM-101A - R-101 Recycle Pumps_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 0 | Read | BOOL | 02
2 | 2202-NK-SG-102-A.03OC_1 | 1115-PM-101A_PERMIT.MCU | MCU.1115-PM-101A - R-101 Recycle Pumps_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 1 | Read | BOOL | 02
3 | 2202-NK-SG-102-A.03OC_1 | 1115-PM-101A_FAULT.MCU | MCU.1115-PM-101A - R-101 Recycle Pumps_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 2 | Read | BOOL | 02
4 | 2202-NK-SG-102-A.03OC_1 | 1115-PM-101A_STA.MCU | MCU.1115-PM-101A - R-101 Recycle Pumps_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 3 | Read | BOOL | 02
5 | 2202-NK-SG-102-A.03OC_1 | 1115-PM-101A_EM_STOP.MCU | MCU.1115-PM-101A - R-101 Recycle Pumps_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 4 | Read | BOOL | 02
6 | 2202-NK-SG-102-A.03OC_1 | 1115-PM-101A_SWITCH_ON.MCU | MCU.1115-PM-101A - R-101 Recycle Pumps_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 5 | Read | BOOL | 02
7 | 2202-NK-SG-102-A.03OC_1 | 1115-PM-101A_MCCB POSITION.MCU | MCU.1115-PM-101A - R-101 Recycle Pumps_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 6 | Read | BOOL | 02
8 | 2202-NK-SG-102-A.03OC_1 | 1115-PM-101A_REDAY.MCU | MCU.1115-PM-101A - R-101 Recycle Pumps_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 7 | Read | BOOL | 02
9 | 2202-NK-SG-102-A.03OC_2 | 1630-PM-214A_TX.MCU | MCU.1630-PM-214A - HP Flare K.O.Drum Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 8 | Read | BOOL | 02
10 | 2202-NK-SG-102-A.03OC_2 | 1630-PM-214A_PERMIT.MCU | MCU.1630-PM-214A - HP Flare K.O.Drum Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 9 | Read | BOOL | 02
11 | 2202-NK-SG-102-A.03OC_2 | 1630-PM-214A_FAULT.MCU | MCU.1630-PM-214A - HP Flare K.O.Drum Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 10 | Read | BOOL | 02
12 | 2202-NK-SG-102-A.03OC_2 | 1630-PM-214A_STA.MCU | MCU.1630-PM-214A - HP Flare K.O.Drum Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 11 | Read | BOOL | 02
13 | 2202-NK-SG-102-A.03OC_2 | 1630-PM-214A_EM_STOP.MCU | MCU.1630-PM-214A - HP Flare K.O.Drum Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 12 | Read | BOOL | 02
14 | 2202-NK-SG-102-A.03OC_2 | 1630-PM-214A_SWITCH_ON.MCU | MCU.1630-PM-214A - HP Flare K.O.Drum Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 13 | Read | BOOL | 02
15 | 2202-NK-SG-102-A.03OC_2 | 1630-PM-214A_MCCB POSITION.MCU | MCU.1630-PM-214A - HP Flare K.O.Drum Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 14 | Read | BOOL | 02
16 | 2202-NK-SG-102-A.03OC_2 | 1630-PM-214A_REDAY.MCU | MCU.1630-PM-214A - HP Flare K.O.Drum Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 15 | Read | BOOL | 02
17 | 2202-NK-SG-102-A.03OC_3 | 1630-PM-605A_TX.MCU | MCU.1630-PM-605A - LP Flare K.O.Drum Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 16 | Read | BOOL | 02
18 | 2202-NK-SG-102-A.03OC_3 | 1630-PM-605A_PERMIT.MCU | MCU.1630-PM-605A - LP Flare K.O.Drum Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 17 | Read | BOOL | 02
19 | 2202-NK-SG-102-A.03OC_3 | 1630-PM-605A_FAULT.MCU | MCU.1630-PM-605A - LP Flare K.O.Drum Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 18 | Read | BOOL | 02
20 | 2202-NK-SG-102-A.03OC_3 | 1630-PM-605A_STA.MCU | MCU.1630-PM-605A - LP Flare K.O.Drum Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 19 | Read | BOOL | 02
21 | 2202-NK-SG-102-A.03OC_3 | 1630-PM-605A_EM_STOP.MCU | MCU.1630-PM-605A - LP Flare K.O.Drum Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 20 | Read | BOOL | 02
22 | 2202-NK-SG-102-A.03OC_3 | 1630-PM-605A_SWITCH_ON.MCU | MCU.1630-PM-605A - LP Flare K.O.Drum Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 21 | Read | BOOL | 02
23 | 2202-NK-SG-102-A.03OC_3 | 1630-PM-605A_MCCB POSITION.MCU | MCU.1630-PM-605A - LP Flare K.O.Drum Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 22 | Read | BOOL | 02
24 | 2202-NK-SG-102-A.03OC_3 | 1630-PM-605A_REDAY.MCU | MCU.1630-PM-605A - LP Flare K.O.Drum Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 23 | Read | BOOL | 02
25 | 2202-NK-SG-102-A.03OC_4 | 1130-PM-305A_TX.MCU | MCU.1130-PM-305A - Offgas Absorber Bottom Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 24 | Read | BOOL | 02
26 | 2202-NK-SG-102-A.03OC_4 | 1130-PM-305A_PERMIT.MCU | MCU.1130-PM-305A - Offgas Absorber Bottom Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 25 | Read | BOOL | 02
27 | 2202-NK-SG-102-A.03OC_4 | 1130-PM-305A_FAULT.MCU | MCU.1130-PM-305A - Offgas Absorber Bottom Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 26 | Read | BOOL | 02
28 | 2202-NK-SG-102-A.03OC_4 | 1130-PM-305A_STA.MCU | MCU.1130-PM-305A - Offgas Absorber Bottom Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 27 | Read | BOOL | 02
29 | 2202-NK-SG-102-A.03OC_4 | 1130-PM-305A_EM_STOP.MCU | MCU.1130-PM-305A - Offgas Absorber Bottom Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 28 | Read | BOOL | 02
30 | 2202-NK-SG-102-A.03OC_4 | 1130-PM-305A_SWITCH_ON.MCU | MCU.1130-PM-305A - Offgas Absorber Bottom Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 29 | Read | BOOL | 02
31 | 2202-NK-SG-102-A.03OC_4 | 1130-PM-305A_MCCB POSITION.MCU | MCU.1130-PM-305A - Offgas Absorber Bottom Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 30 | Read | BOOL | 02
32 | 2202-NK-SG-102-A.03OC_4 | 1130-PM-305A_REDAY.MCU | MCU.1130-PM-305A - Offgas Absorber Bottom Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 31 | Read | BOOL | 02
33 | 2202-NK-SG-102-A.03OC_5 | 1130-PM-306A_TX.MCU | MCU.1130-PM-306A - Rich Oil Stripper Bottom Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 32 | Read | BOOL | 02
34 | 2202-NK-SG-102-A.03OC_5 | 1130-PM-306A_PERMIT.MCU | MCU.1130-PM-306A - Rich Oil Stripper Bottom Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 33 | Read | BOOL | 02
35 | 2202-NK-SG-102-A.03OC_5 | 1130-PM-306A_FAULT.MCU | MCU.1130-PM-306A - Rich Oil Stripper Bottom Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 34 | Read | BOOL | 02
36 | 2202-NK-SG-102-A.03OC_5 | 1130-PM-306A_STA.MCU | MCU.1130-PM-306A - Rich Oil Stripper Bottom Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 35 | Read | BOOL | 02
37 | 2202-NK-SG-102-A.03OC_5 | 1130-PM-306A_EM_STOP.MCU | MCU.1130-PM-306A - Rich Oil Stripper Bottom Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 36 | Read | BOOL | 02
38 | 2202-NK-SG-102-A.03OC_5 | 1130-PM-306A_SWITCH_ON.MCU | MCU.1130-PM-306A - Rich Oil Stripper Bottom Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 37 | Read | BOOL | 02
39 | 2202-NK-SG-102-A.03OC_5 | 1130-PM-306A_MCCB POSITION.MCU | MCU.1130-PM-306A - Rich Oil Stripper Bottom Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 38 | Read | BOOL | 02
40 | 2202-NK-SG-102-A.03OC_5 | 1130-PM-306A_REDAY.MCU | MCU.1130-PM-306A - Rich Oil Stripper Bottom Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 39 | Read | BOOL | 02
41 | 2202-NK-SG-102-A.03OC_6 | 1162-PM-602_TX.MCU | MCU.1162-PM-602 - SM Slop Drum water Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 40 | Read | BOOL | 02
42 | 2202-NK-SG-102-A.03OC_6 | 1162-PM-602_PERMIT.MCU | MCU.1162-PM-602 - SM Slop Drum water Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 41 | Read | BOOL | 02
43 | 2202-NK-SG-102-A.03OC_6 | 1162-PM-602_FAULT.MCU | MCU.1162-PM-602 - SM Slop Drum water Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 42 | Read | BOOL | 02
44 | 2202-NK-SG-102-A.03OC_6 | 1162-PM-602_STA.MCU | MCU.1162-PM-602 - SM Slop Drum water Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 43 | Read | BOOL | 02
45 | 2202-NK-SG-102-A.03OC_6 | 1162-PM-602_EM_STOP.MCU | MCU.1162-PM-602 - SM Slop Drum water Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 44 | Read | BOOL | 02
46 | 2202-NK-SG-102-A.03OC_6 | 1162-PM-602_SWITCH_ON.MCU | MCU.1162-PM-602 - SM Slop Drum water Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 45 | Read | BOOL | 02
47 | 2202-NK-SG-102-A.03OC_6 | 1162-PM-602_MCCB POSITION.MCU | MCU.1162-PM-602 - SM Slop Drum water Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 46 | Read | BOOL | 02
48 | 2202-NK-SG-102-A.03OC_6 | 1162-PM-602_REDAY.MCU | MCU.1162-PM-602 - SM Slop Drum water Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 47 | Read | BOOL | 02
49 | 2202-NK-SG-102-A.03OC_7 | 1162-PM-603_TX.MCU | MCU.1162-PM-603 - SM Slop Drum HC Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 48 | Read | BOOL | 02
50 | 2202-NK-SG-102-A.03OC_7 | 1162-PM-603_PERMIT.MCU | MCU.1162-PM-603 - SM Slop Drum HC Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 49 | Read | BOOL | 02
51 | 2202-NK-SG-102-A.03OC_7 | 1162-PM-603_FAULT.MCU | MCU.1162-PM-603 - SM Slop Drum HC Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 50 | Read | BOOL | 02
52 | 2202-NK-SG-102-A.03OC_7 | 1162-PM-603_STA.MCU | MCU.1162-PM-603 - SM Slop Drum HC Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 51 | Read | BOOL | 02
53 | 2202-NK-SG-102-A.03OC_7 | 1162-PM-603_EM_STOP.MCU | MCU.1162-PM-603 - SM Slop Drum HC Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 52 | Read | BOOL | 02
54 | 2202-NK-SG-102-A.03OC_7 | 1162-PM-603_SWITCH_ON.MCU | MCU.1162-PM-603 - SM Slop Drum HC Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 53 | Read | BOOL | 02
55 | 2202-NK-SG-102-A.03OC_7 | 1162-PM-603_MCCB POSITION.MCU | MCU.1162-PM-603 - SM Slop Drum HC Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 54 | Read | BOOL | 02
56 | 2202-NK-SG-102-A.03OC_7 | 1162-PM-603_REDAY.MCU | MCU.1162-PM-603 - SM Slop Drum HC Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 55 | Read | BOOL | 02
57 | 2202-NK-SG-102-A.03OC_8 | 2202-NK-SG-102-A.03OC_8_TX.MCU | MCU.2202-NK-SG-102-A.03OC_8 - SPARE_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 56 | Read | BOOL | 02
58 | 2202-NK-SG-102-A.03OC_8 | 2202-NK-SG-102-A.03OC_8_PERMIT.MCU | MCU.2202-NK-SG-102-A.03OC_8 - SPARE_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 57 | Read | BOOL | 02
59 | 2202-NK-SG-102-A.03OC_8 | 2202-NK-SG-102-A.03OC_8_FAULT.MCU | MCU.2202-NK-SG-102-A.03OC_8 - SPARE_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 58 | Read | BOOL | 02
60 | 2202-NK-SG-102-A.03OC_8 | 2202-NK-SG-102-A.03OC_8_STA.MCU | MCU.2202-NK-SG-102-A.03OC_8 - SPARE_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 59 | Read | BOOL | 02
61 | 2202-NK-SG-102-A.03OC_8 | 2202-NK-SG-102-A.03OC_8_EM_STOP.MCU | MCU.2202-NK-SG-102-A.03OC_8 - SPARE_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 60 | Read | BOOL | 02
62 | 2202-NK-SG-102-A.03OC_8 | 2202-NK-SG-102-A.03OC_8_SWITCH_ON.MCU | MCU.2202-NK-SG-102-A.03OC_8 - SPARE_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 61 | Read | BOOL | 02
63 | 2202-NK-SG-102-A.03OC_8 | 2202-NK-SG-102-A.03OC_8_MCCB POSITION.MCU | MCU.2202-NK-SG-102-A.03OC_8 - SPARE_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 62 | Read | BOOL | 02
64 | 2202-NK-SG-102-A.03OC_8 | 2202-NK-SG-102-A.03OC_8_REDAY.MCU | MCU.2202-NK-SG-102-A.03OC_8 - SPARE_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 63 | Read | BOOL | 02
65 | 2202-NK-SG-102-A.05OC_1 | 1130-PM-311_TX.MCU | MCU.1130-PM-311 - Back-washed pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 64 | Read | BOOL | 02
66 | 2202-NK-SG-102-A.05OC_1 | 1130-PM-311_PERMIT.MCU | MCU.1130-PM-311 - Back-washed pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 65 | Read | BOOL | 02
67 | 2202-NK-SG-102-A.05OC_1 | 1130-PM-311_FAULT.MCU | MCU.1130-PM-311 - Back-washed pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 66 | Read | BOOL | 02
68 | 2202-NK-SG-102-A.05OC_1 | 1130-PM-311_STA.MCU | MCU.1130-PM-311 - Back-washed pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 67 | Read | BOOL | 02
69 | 2202-NK-SG-102-A.05OC_1 | 1130-PM-311_EM_STOP.MCU | MCU.1130-PM-311 - Back-washed pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 68 | Read | BOOL | 02
70 | 2202-NK-SG-102-A.05OC_1 | 1130-PM-311_SWITCH_ON.MCU | MCU.1130-PM-311 - Back-washed pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 69 | Read | BOOL | 02
71 | 2202-NK-SG-102-A.05OC_1 | 1130-PM-311_MCCB POSITION.MCU | MCU.1130-PM-311 - Back-washed pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 70 | Read | BOOL | 02
72 | 2202-NK-SG-102-A.05OC_1 | 1130-PM-311_REDAY.MCU | MCU.1130-PM-311 - Back-washed pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 71 | Read | BOOL | 02
73 | 2202-NK-SG-102-A.05OC_2 | 1612-PM-611A_TX.MCU | MCU.1612-PM-611A - Desuperheater Water Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 72 | Read | BOOL | 02
74 | 2202-NK-SG-102-A.05OC_2 | 1612-PM-611A_PERMIT.MCU | MCU.1612-PM-611A - Desuperheater Water Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 73 | Read | BOOL | 02
75 | 2202-NK-SG-102-A.05OC_2 | 1612-PM-611A_FAULT.MCU | MCU.1612-PM-611A - Desuperheater Water Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 74 | Read | BOOL | 02
76 | 2202-NK-SG-102-A.05OC_2 | 1612-PM-611A_STA.MCU | MCU.1612-PM-611A - Desuperheater Water Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 75 | Read | BOOL | 02
77 | 2202-NK-SG-102-A.05OC_2 | 1612-PM-611A_EM_STOP.MCU | MCU.1612-PM-611A - Desuperheater Water Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 76 | Read | BOOL | 02
78 | 2202-NK-SG-102-A.05OC_2 | 1612-PM-611A_SWITCH_ON.MCU | MCU.1612-PM-611A - Desuperheater Water Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 77 | Read | BOOL | 02
79 | 2202-NK-SG-102-A.05OC_2 | 1612-PM-611A_MCCB POSITION.MCU | MCU.1612-PM-611A - Desuperheater Water Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 78 | Read | BOOL | 02
80 | 2202-NK-SG-102-A.05OC_2 | 1612-PM-611A_REDAY.MCU | MCU.1612-PM-611A - Desuperheater Water Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 79 | Read | BOOL | 02
81 | 2202-NK-SG-102-A.05OC_3 | 1612-PM-001A_TX.MCU | MCU.1612-PM-001A - oil pump motor_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 80 | Read | BOOL | 02
82 | 2202-NK-SG-102-A.05OC_3 | 1612-PM-001A_PERMIT.MCU | MCU.1612-PM-001A - oil pump motor_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 81 | Read | BOOL | 02
83 | 2202-NK-SG-102-A.05OC_3 | 1612-PM-001A_FAULT.MCU | MCU.1612-PM-001A - oil pump motor_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 82 | Read | BOOL | 02
84 | 2202-NK-SG-102-A.05OC_3 | 1612-PM-001A_STA.MCU | MCU.1612-PM-001A - oil pump motor_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 83 | Read | BOOL | 02
85 | 2202-NK-SG-102-A.05OC_3 | 1612-PM-001A_EM_STOP.MCU | MCU.1612-PM-001A - oil pump motor_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 84 | Read | BOOL | 02
86 | 2202-NK-SG-102-A.05OC_3 | 1612-PM-001A_SWITCH_ON.MCU | MCU.1612-PM-001A - oil pump motor_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 85 | Read | BOOL | 02
87 | 2202-NK-SG-102-A.05OC_3 | 1612-PM-001A_MCCB POSITION.MCU | MCU.1612-PM-001A - oil pump motor_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 86 | Read | BOOL | 02
88 | 2202-NK-SG-102-A.05OC_3 | 1612-PM-001A_REDAY.MCU | MCU.1612-PM-001A - oil pump motor_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 87 | Read | BOOL | 02
89 | 2202-NK-SG-102-A.05OC_4 | 1612-P-611A.HE-JB_TX.MCU | MCU.1612-P-611A.HE-JB - Oil heater junction box_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 88 | Read | BOOL | 02
90 | 2202-NK-SG-102-A.05OC_4 | 1612-P-611A.HE-JB_PERMIT.MCU | MCU.1612-P-611A.HE-JB - Oil heater junction box_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 89 | Read | BOOL | 02
91 | 2202-NK-SG-102-A.05OC_4 | 1612-P-611A.HE-JB_FAULT.MCU | MCU.1612-P-611A.HE-JB - Oil heater junction box_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 90 | Read | BOOL | 02
92 | 2202-NK-SG-102-A.05OC_4 | 1612-P-611A.HE-JB_STA.MCU | MCU.1612-P-611A.HE-JB - Oil heater junction box_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 91 | Read | BOOL | 02
93 | 2202-NK-SG-102-A.05OC_4 | 1612-P-611A.HE-JB_EM_STOP.MCU | MCU.1612-P-611A.HE-JB - Oil heater junction box_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 92 | Read | BOOL | 02
94 | 2202-NK-SG-102-A.05OC_4 | 1612-P-611A.HE-JB_SWITCH_ON.MCU | MCU.1612-P-611A.HE-JB - Oil heater junction box_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 93 | Read | BOOL | 02
95 | 2202-NK-SG-102-A.05OC_4 | 1612-P-611A.HE-JB_MCCB POSITION.MCU | MCU.1612-P-611A.HE-JB - Oil heater junction box_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 94 | Read | BOOL | 02
96 | 2202-NK-SG-102-A.05OC_4 | 1612-P-611A.HE-JB_REDAY.MCU | MCU.1612-P-611A.HE-JB - Oil heater junction box_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 95 | Read | BOOL | 02
97 | 2202-NK-SG-102-A.05OC_5 | 1624-PM-614_TX.MCU | MCU.1624-PM-614 - Wasteoil Sump Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 96 | Read | BOOL | 02
98 | 2202-NK-SG-102-A.05OC_5 | 1624-PM-614_PERMIT.MCU | MCU.1624-PM-614 - Wasteoil Sump Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 97 | Read | BOOL | 02
99 | 2202-NK-SG-102-A.05OC_5 | 1624-PM-614_FAULT.MCU | MCU.1624-PM-614 - Wasteoil Sump Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 98 | Read | BOOL | 02
100 | 2202-NK-SG-102-A.05OC_5 | 1624-PM-614_STA.MCU | MCU.1624-PM-614 - Wasteoil Sump Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 99 | Read | BOOL | 02
101 | 2202-NK-SG-102-A.05OC_5 | 1624-PM-614_EM_STOP.MCU | MCU.1624-PM-614 - Wasteoil Sump Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 100 | Read | BOOL | 02
102 | 2202-NK-SG-102-A.05OC_5 | 1624-PM-614_SWITCH_ON.MCU | MCU.1624-PM-614 - Wasteoil Sump Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 101 | Read | BOOL | 02
103 | 2202-NK-SG-102-A.05OC_5 | 1624-PM-614_MCCB POSITION.MCU | MCU.1624-PM-614 - Wasteoil Sump Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 102 | Read | BOOL | 02
104 | 2202-NK-SG-102-A.05OC_5 | 1624-PM-614_REDAY.MCU | MCU.1624-PM-614 - Wasteoil Sump Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 103 | Read | BOOL | 02
105 | 2202-NK-SG-102-A.05OC_6 | 2202-NK-SG-102-A.05OC_6_TX.MCU | MCU.2202-NK-SG-102-A.05OC_6 - SPARE_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 104 | Read | BOOL | 02
106 | 2202-NK-SG-102-A.05OC_6 | 2202-NK-SG-102-A.05OC_6_PERMIT.MCU | MCU.2202-NK-SG-102-A.05OC_6 - SPARE_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 105 | Read | BOOL | 02
107 | 2202-NK-SG-102-A.05OC_6 | 2202-NK-SG-102-A.05OC_6_FAULT.MCU | MCU.2202-NK-SG-102-A.05OC_6 - SPARE_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 106 | Read | BOOL | 02
108 | 2202-NK-SG-102-A.05OC_6 | 2202-NK-SG-102-A.05OC_6_STA.MCU | MCU.2202-NK-SG-102-A.05OC_6 - SPARE_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 107 | Read | BOOL | 02
109 | 2202-NK-SG-102-A.05OC_6 | 2202-NK-SG-102-A.05OC_6_EM_STOP.MCU | MCU.2202-NK-SG-102-A.05OC_6 - SPARE_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 108 | Read | BOOL | 02
110 | 2202-NK-SG-102-A.05OC_6 | 2202-NK-SG-102-A.05OC_6_SWITCH_ON.MCU | MCU.2202-NK-SG-102-A.05OC_6 - SPARE_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 109 | Read | BOOL | 02
111 | 2202-NK-SG-102-A.05OC_6 | 2202-NK-SG-102-A.05OC_6_MCCB POSITION.MCU | MCU.2202-NK-SG-102-A.05OC_6 - SPARE_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 110 | Read | BOOL | 02
112 | 2202-NK-SG-102-A.05OC_6 | 2202-NK-SG-102-A.05OC_6_REDAY.MCU | MCU.2202-NK-SG-102-A.05OC_6 - SPARE_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 111 | Read | BOOL | 02
113 | 2202-NK-SG-102-A.05OC_7 | 1130-PM-302A_TX.MCU | MCU.1130-PM-302A - Process Condensate Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 112 | Read | BOOL | 02
114 | 2202-NK-SG-102-A.05OC_7 | 1130-PM-302A_PERMIT.MCU | MCU.1130-PM-302A - Process Condensate Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 113 | Read | BOOL | 02
115 | 2202-NK-SG-102-A.05OC_7 | 1130-PM-302A_FAULT.MCU | MCU.1130-PM-302A - Process Condensate Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 114 | Read | BOOL | 02
116 | 2202-NK-SG-102-A.05OC_7 | 1130-PM-302A_STA.MCU | MCU.1130-PM-302A - Process Condensate Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 115 | Read | BOOL | 02
117 | 2202-NK-SG-102-A.05OC_7 | 1130-PM-302A_EM_STOP.MCU | MCU.1130-PM-302A - Process Condensate Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 116 | Read | BOOL | 02
118 | 2202-NK-SG-102-A.05OC_7 | 1130-PM-302A_SWITCH_ON.MCU | MCU.1130-PM-302A - Process Condensate Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 117 | Read | BOOL | 02
119 | 2202-NK-SG-102-A.05OC_7 | 1130-PM-302A_MCCB POSITION.MCU | MCU.1130-PM-302A - Process Condensate Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 118 | Read | BOOL | 02
120 | 2202-NK-SG-102-A.05OC_7 | 1130-PM-302A_REDAY.MCU | MCU.1130-PM-302A - Process Condensate Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 119 | Read | BOOL | 02
121 | 2202-NK-SG-102-A.07OC_1 | 1110-KM-101A-2_TX.MCU | MCU.1110-KM-101A-2 - Barring motor_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 120 | Read | BOOL | 02
122 | 2202-NK-SG-102-A.07OC_1 | 1110-KM-101A-2_PERMIT.MCU | MCU.1110-KM-101A-2 - Barring motor_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 121 | Read | BOOL | 02
123 | 2202-NK-SG-102-A.07OC_1 | 1110-KM-101A-2_FAULT.MCU | MCU.1110-KM-101A-2 - Barring motor_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 122 | Read | BOOL | 02
124 | 2202-NK-SG-102-A.07OC_1 | 1110-KM-101A-2_STA.MCU | MCU.1110-KM-101A-2 - Barring motor_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 123 | Read | BOOL | 02
125 | 2202-NK-SG-102-A.07OC_1 | 1110-KM-101A-2_EM_STOP.MCU | MCU.1110-KM-101A-2 - Barring motor_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 124 | Read | BOOL | 02
126 | 2202-NK-SG-102-A.07OC_1 | 1110-KM-101A-2_SWITCH_ON.MCU | MCU.1110-KM-101A-2 - Barring motor_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 125 | Read | BOOL | 02
127 | 2202-NK-SG-102-A.07OC_1 | 1110-KM-101A-2_MCCB POSITION.MCU | MCU.1110-KM-101A-2 - Barring motor_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 126 | Read | BOOL | 02
128 | 2202-NK-SG-102-A.07OC_1 | 1110-KM-101A-2_REDAY.MCU | MCU.1110-KM-101A-2 - Barring motor_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 127 | Read | BOOL | 02
129 | 2202-NK-SG-102-A.07OC_2 | 1110-PM-131A_TX.MCU | MCU.1110-PM-131A - Oil pump motor 1_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 128 | Read | BOOL | 02
130 | 2202-NK-SG-102-A.07OC_2 | 1110-PM-131A_PERMIT.MCU | MCU.1110-PM-131A - Oil pump motor 1_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 129 | Read | BOOL | 02
131 | 2202-NK-SG-102-A.07OC_2 | 1110-PM-131A_FAULT.MCU | MCU.1110-PM-131A - Oil pump motor 1_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 130 | Read | BOOL | 02
132 | 2202-NK-SG-102-A.07OC_2 | 1110-PM-131A_STA.MCU | MCU.1110-PM-131A - Oil pump motor 1_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 131 | Read | BOOL | 02
133 | 2202-NK-SG-102-A.07OC_2 | 1110-PM-131A_EM_STOP.MCU | MCU.1110-PM-131A - Oil pump motor 1_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 132 | Read | BOOL | 02
134 | 2202-NK-SG-102-A.07OC_2 | 1110-PM-131A_SWITCH_ON.MCU | MCU.1110-PM-131A - Oil pump motor 1_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 133 | Read | BOOL | 02
135 | 2202-NK-SG-102-A.07OC_2 | 1110-PM-131A_MCCB POSITION.MCU | MCU.1110-PM-131A - Oil pump motor 1_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 134 | Read | BOOL | 02
136 | 2202-NK-SG-102-A.07OC_2 | 1110-PM-131A_REDAY.MCU | MCU.1110-PM-131A - Oil pump motor 1_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 135 | Read | BOOL | 02
137 | 2202-NK-SG-102-A.07OC_3 | 1110-PM-131B_TX.MCU | MCU.1110-PM-131B - Oil pump motor 2_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 136 | Read | BOOL | 02
138 | 2202-NK-SG-102-A.07OC_3 | 1110-PM-131B_PERMIT.MCU | MCU.1110-PM-131B - Oil pump motor 2_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 137 | Read | BOOL | 02
139 | 2202-NK-SG-102-A.07OC_3 | 1110-PM-131B_FAULT.MCU | MCU.1110-PM-131B - Oil pump motor 2_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 138 | Read | BOOL | 02
140 | 2202-NK-SG-102-A.07OC_3 | 1110-PM-131B_STA.MCU | MCU.1110-PM-131B - Oil pump motor 2_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 139 | Read | BOOL | 02
141 | 2202-NK-SG-102-A.07OC_3 | 1110-PM-131B_EM_STOP.MCU | MCU.1110-PM-131B - Oil pump motor 2_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 140 | Read | BOOL | 02
142 | 2202-NK-SG-102-A.07OC_3 | 1110-PM-131B_SWITCH_ON.MCU | MCU.1110-PM-131B - Oil pump motor 2_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 141 | Read | BOOL | 02
143 | 2202-NK-SG-102-A.07OC_3 | 1110-PM-131B_MCCB POSITION.MCU | MCU.1110-PM-131B - Oil pump motor 2_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 142 | Read | BOOL | 02
144 | 2202-NK-SG-102-A.07OC_3 | 1110-PM-131B_REDAY.MCU | MCU.1110-PM-131B - Oil pump motor 2_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 143 | Read | BOOL | 02
145 | 2202-NK-SG-102-A.07OC_4 | 1110-KM-101A.EH02_TX.MCU | MCU.1110-KM-101A.EH02 - Electric heater for crankcase_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 144 | Read | BOOL | 02
146 | 2202-NK-SG-102-A.07OC_4 | 1110-KM-101A.EH02_PERMIT.MCU | MCU.1110-KM-101A.EH02 - Electric heater for crankcase_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 145 | Read | BOOL | 02
147 | 2202-NK-SG-102-A.07OC_4 | 1110-KM-101A.EH02_FAULT.MCU | MCU.1110-KM-101A.EH02 - Electric heater for crankcase_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 146 | Read | BOOL | 02
148 | 2202-NK-SG-102-A.07OC_4 | 1110-KM-101A.EH02_STA.MCU | MCU.1110-KM-101A.EH02 - Electric heater for crankcase_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 147 | Read | BOOL | 02
149 | 2202-NK-SG-102-A.07OC_4 | 1110-KM-101A.EH02_EM_STOP.MCU | MCU.1110-KM-101A.EH02 - Electric heater for crankcase_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 148 | Read | BOOL | 02
150 | 2202-NK-SG-102-A.07OC_4 | 1110-KM-101A.EH02_SWITCH_ON.MCU | MCU.1110-KM-101A.EH02 - Electric heater for crankcase_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 149 | Read | BOOL | 02
151 | 2202-NK-SG-102-A.07OC_4 | 1110-KM-101A.EH02_MCCB POSITION.MCU | MCU.1110-KM-101A.EH02 - Electric heater for crankcase_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 150 | Read | BOOL | 02
152 | 2202-NK-SG-102-A.07OC_4 | 1110-KM-101A.EH02_REDAY.MCU | MCU.1110-KM-101A.EH02 - Electric heater for crankcase_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 151 | Read | BOOL | 02
153 | 2202-NK-SG-102-A.07OC_5 | 1110-PM-133A_TX.MCU | MCU.1110-PM-133A - Water pump motor 1_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 152 | Read | BOOL | 02
154 | 2202-NK-SG-102-A.07OC_5 | 1110-PM-133A_PERMIT.MCU | MCU.1110-PM-133A - Water pump motor 1_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 153 | Read | BOOL | 02
155 | 2202-NK-SG-102-A.07OC_5 | 1110-PM-133A_FAULT.MCU | MCU.1110-PM-133A - Water pump motor 1_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 154 | Read | BOOL | 02
156 | 2202-NK-SG-102-A.07OC_5 | 1110-PM-133A_STA.MCU | MCU.1110-PM-133A - Water pump motor 1_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 155 | Read | BOOL | 02
157 | 2202-NK-SG-102-A.07OC_5 | 1110-PM-133A_EM_STOP.MCU | MCU.1110-PM-133A - Water pump motor 1_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 156 | Read | BOOL | 02
158 | 2202-NK-SG-102-A.07OC_5 | 1110-PM-133A_SWITCH_ON.MCU | MCU.1110-PM-133A - Water pump motor 1_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 157 | Read | BOOL | 02
159 | 2202-NK-SG-102-A.07OC_5 | 1110-PM-133A_MCCB POSITION.MCU | MCU.1110-PM-133A - Water pump motor 1_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 158 | Read | BOOL | 02
160 | 2202-NK-SG-102-A.07OC_5 | 1110-PM-133A_REDAY.MCU | MCU.1110-PM-133A - Water pump motor 1_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 159 | Read | BOOL | 02
161 | 2202-NK-SG-102-A.07OC_6 | 1110-V-136.EH_TX.MCU | MCU.1110-V-136.EH - Electric heater for water tank_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 160 | Read | BOOL | 02
162 | 2202-NK-SG-102-A.07OC_6 | 1110-V-136.EH_PERMIT.MCU | MCU.1110-V-136.EH - Electric heater for water tank_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 161 | Read | BOOL | 02
163 | 2202-NK-SG-102-A.07OC_6 | 1110-V-136.EH_FAULT.MCU | MCU.1110-V-136.EH - Electric heater for water tank_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 162 | Read | BOOL | 02
164 | 2202-NK-SG-102-A.07OC_6 | 1110-V-136.EH_STA.MCU | MCU.1110-V-136.EH - Electric heater for water tank_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 163 | Read | BOOL | 02
165 | 2202-NK-SG-102-A.07OC_6 | 1110-V-136.EH_EM_STOP.MCU | MCU.1110-V-136.EH - Electric heater for water tank_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 164 | Read | BOOL | 02
166 | 2202-NK-SG-102-A.07OC_6 | 1110-V-136.EH_SWITCH_ON.MCU | MCU.1110-V-136.EH - Electric heater for water tank_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 165 | Read | BOOL | 02
167 | 2202-NK-SG-102-A.07OC_6 | 1110-V-136.EH_MCCB POSITION.MCU | MCU.1110-V-136.EH - Electric heater for water tank_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 166 | Read | BOOL | 02
168 | 2202-NK-SG-102-A.07OC_6 | 1110-V-136.EH_REDAY.MCU | MCU.1110-V-136.EH - Electric heater for water tank_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 167 | Read | BOOL | 02
169 | 2202-NK-SG-102-A.07OC_7 | 1130-KM-301A_TX.MCU | MCU.1130-KM-301A - Barring motor_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 168 | Read | BOOL | 02
170 | 2202-NK-SG-102-A.07OC_7 | 1130-KM-301A_PERMIT.MCU | MCU.1130-KM-301A - Barring motor_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 169 | Read | BOOL | 02
171 | 2202-NK-SG-102-A.07OC_7 | 1130-KM-301A_FAULT.MCU | MCU.1130-KM-301A - Barring motor_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 170 | Read | BOOL | 02
172 | 2202-NK-SG-102-A.07OC_7 | 1130-KM-301A_STA.MCU | MCU.1130-KM-301A - Barring motor_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 171 | Read | BOOL | 02
173 | 2202-NK-SG-102-A.07OC_7 | 1130-KM-301A_EM_STOP.MCU | MCU.1130-KM-301A - Barring motor_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 172 | Read | BOOL | 02
174 | 2202-NK-SG-102-A.07OC_7 | 1130-KM-301A_SWITCH_ON.MCU | MCU.1130-KM-301A - Barring motor_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 173 | Read | BOOL | 02
175 | 2202-NK-SG-102-A.07OC_7 | 1130-KM-301A_MCCB POSITION.MCU | MCU.1130-KM-301A - Barring motor_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 174 | Read | BOOL | 02
176 | 2202-NK-SG-102-A.07OC_7 | 1130-KM-301A_REDAY.MCU | MCU.1130-KM-301A - Barring motor_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 175 | Read | BOOL | 02
177 | 2202-NK-SG-102-A.07OC_8 | 2202-NK-SG-102-A.07OC_8_TX.MCU | MCU.2202-NK-SG-102-A.07OC_8 - SPARE_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 176 | Read | BOOL | 02
178 | 2202-NK-SG-102-A.07OC_8 | 2202-NK-SG-102-A.07OC_8_PERMIT.MCU | MCU.2202-NK-SG-102-A.07OC_8 - SPARE_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 177 | Read | BOOL | 02
179 | 2202-NK-SG-102-A.07OC_8 | 2202-NK-SG-102-A.07OC_8_FAULT.MCU | MCU.2202-NK-SG-102-A.07OC_8 - SPARE_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 178 | Read | BOOL | 02
180 | 2202-NK-SG-102-A.07OC_8 | 2202-NK-SG-102-A.07OC_8_STA.MCU | MCU.2202-NK-SG-102-A.07OC_8 - SPARE_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 179 | Read | BOOL | 02
181 | 2202-NK-SG-102-A.07OC_8 | 2202-NK-SG-102-A.07OC_8_EM_STOP.MCU | MCU.2202-NK-SG-102-A.07OC_8 - SPARE_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 180 | Read | BOOL | 02
182 | 2202-NK-SG-102-A.07OC_8 | 2202-NK-SG-102-A.07OC_8_SWITCH_ON.MCU | MCU.2202-NK-SG-102-A.07OC_8 - SPARE_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 181 | Read | BOOL | 02
183 | 2202-NK-SG-102-A.07OC_8 | 2202-NK-SG-102-A.07OC_8_MCCB POSITION.MCU | MCU.2202-NK-SG-102-A.07OC_8 - SPARE_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 182 | Read | BOOL | 02
184 | 2202-NK-SG-102-A.07OC_8 | 2202-NK-SG-102-A.07OC_8_REDAY.MCU | MCU.2202-NK-SG-102-A.07OC_8 - SPARE_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 183 | Read | BOOL | 02
185 | 2202-NK-SG-102-A.09OC_1 | 1130-BLM-331A_TX.MCU | MCU.1130-BLM-331A - Oil station fans_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 184 | Read | BOOL | 02
186 | 2202-NK-SG-102-A.09OC_1 | 1130-BLM-331A_PERMIT.MCU | MCU.1130-BLM-331A - Oil station fans_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 185 | Read | BOOL | 02
187 | 2202-NK-SG-102-A.09OC_1 | 1130-BLM-331A_FAULT.MCU | MCU.1130-BLM-331A - Oil station fans_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 186 | Read | BOOL | 02
188 | 2202-NK-SG-102-A.09OC_1 | 1130-BLM-331A_STA.MCU | MCU.1130-BLM-331A - Oil station fans_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 187 | Read | BOOL | 02
189 | 2202-NK-SG-102-A.09OC_1 | 1130-BLM-331A_EM_STOP.MCU | MCU.1130-BLM-331A - Oil station fans_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 188 | Read | BOOL | 02
190 | 2202-NK-SG-102-A.09OC_1 | 1130-BLM-331A_SWITCH_ON.MCU | MCU.1130-BLM-331A - Oil station fans_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 189 | Read | BOOL | 02
191 | 2202-NK-SG-102-A.09OC_1 | 1130-BLM-331A_MCCB POSITION.MCU | MCU.1130-BLM-331A - Oil station fans_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 190 | Read | BOOL | 02
192 | 2202-NK-SG-102-A.09OC_1 | 1130-BLM-331A_REDAY.MCU | MCU.1130-BLM-331A - Oil station fans_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 191 | Read | BOOL | 02
193 | 2202-NK-SG-102-A.09OC_2 | 1130-PM-331B_TX.MCU | MCU.1130-PM-331B - Auxiliary oil pump motor_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 192 | Read | BOOL | 02
194 | 2202-NK-SG-102-A.09OC_2 | 1130-PM-331B_PERMIT.MCU | MCU.1130-PM-331B - Auxiliary oil pump motor_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 193 | Read | BOOL | 02
195 | 2202-NK-SG-102-A.09OC_2 | 1130-PM-331B_FAULT.MCU | MCU.1130-PM-331B - Auxiliary oil pump motor_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 194 | Read | BOOL | 02
196 | 2202-NK-SG-102-A.09OC_2 | 1130-PM-331B_STA.MCU | MCU.1130-PM-331B - Auxiliary oil pump motor_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 195 | Read | BOOL | 02
197 | 2202-NK-SG-102-A.09OC_2 | 1130-PM-331B_EM_STOP.MCU | MCU.1130-PM-331B - Auxiliary oil pump motor_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 196 | Read | BOOL | 02
198 | 2202-NK-SG-102-A.09OC_2 | 1130-PM-331B_SWITCH_ON.MCU | MCU.1130-PM-331B - Auxiliary oil pump motor_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 197 | Read | BOOL | 02
199 | 2202-NK-SG-102-A.09OC_2 | 1130-PM-331B_MCCB POSITION.MCU | MCU.1130-PM-331B - Auxiliary oil pump motor_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 198 | Read | BOOL | 02
200 | 2202-NK-SG-102-A.09OC_2 | 1130-PM-331B_REDAY.MCU | MCU.1130-PM-331B - Auxiliary oil pump motor_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 199 | Read | BOOL | 02
201 | 2202-NK-SG-102-A.09OC_3 | 1130-V-332A.EH_TX.MCU | MCU.1130-V-332A.EH - Lube oil tank heater_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 200 | Read | BOOL | 02
202 | 2202-NK-SG-102-A.09OC_3 | 1130-V-332A.EH_PERMIT.MCU | MCU.1130-V-332A.EH - Lube oil tank heater_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 201 | Read | BOOL | 02
203 | 2202-NK-SG-102-A.09OC_3 | 1130-V-332A.EH_FAULT.MCU | MCU.1130-V-332A.EH - Lube oil tank heater_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 202 | Read | BOOL | 02
204 | 2202-NK-SG-102-A.09OC_3 | 1130-V-332A.EH_STA.MCU | MCU.1130-V-332A.EH - Lube oil tank heater_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 203 | Read | BOOL | 02
205 | 2202-NK-SG-102-A.09OC_3 | 1130-V-332A.EH_EM_STOP.MCU | MCU.1130-V-332A.EH - Lube oil tank heater_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 204 | Read | BOOL | 02
206 | 2202-NK-SG-102-A.09OC_3 | 1130-V-332A.EH_SWITCH_ON.MCU | MCU.1130-V-332A.EH - Lube oil tank heater_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 205 | Read | BOOL | 02
207 | 2202-NK-SG-102-A.09OC_3 | 1130-V-332A.EH_MCCB POSITION.MCU | MCU.1130-V-332A.EH - Lube oil tank heater_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 206 | Read | BOOL | 02
208 | 2202-NK-SG-102-A.09OC_3 | 1130-V-332A.EH_REDAY.MCU | MCU.1130-V-332A.EH - Lube oil tank heater_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 207 | Read | BOOL | 02
209 | 2202-NK-SG-102-A.09OC_4 | 1130-PM-331A_TX.MCU | MCU.1130-PM-331A - Main oil pump motor_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 208 | Read | BOOL | 02
210 | 2202-NK-SG-102-A.09OC_4 | 1130-PM-331A_PERMIT.MCU | MCU.1130-PM-331A - Main oil pump motor_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 209 | Read | BOOL | 02
211 | 2202-NK-SG-102-A.09OC_4 | 1130-PM-331A_FAULT.MCU | MCU.1130-PM-331A - Main oil pump motor_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 210 | Read | BOOL | 02
212 | 2202-NK-SG-102-A.09OC_4 | 1130-PM-331A_STA.MCU | MCU.1130-PM-331A - Main oil pump motor_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 211 | Read | BOOL | 02
213 | 2202-NK-SG-102-A.09OC_4 | 1130-PM-331A_EM_STOP.MCU | MCU.1130-PM-331A - Main oil pump motor_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 212 | Read | BOOL | 02
214 | 2202-NK-SG-102-A.09OC_4 | 1130-PM-331A_SWITCH_ON.MCU | MCU.1130-PM-331A - Main oil pump motor_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 213 | Read | BOOL | 02
215 | 2202-NK-SG-102-A.09OC_4 | 1130-PM-331A_MCCB POSITION.MCU | MCU.1130-PM-331A - Main oil pump motor_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 214 | Read | BOOL | 02
216 | 2202-NK-SG-102-A.09OC_4 | 1130-PM-331A_REDAY.MCU | MCU.1130-PM-331A - Main oil pump motor_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 215 | Read | BOOL | 02
217 | 2202-NK-SG-102-A.11OC_3 | 2701-PK-1501A-M_TX.MCU | MCU.2701-PK-1501A-M - ITF Waste Gas FanAcoustic Enclosure Fan_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 216 | Read | BOOL | 02
218 | 2202-NK-SG-102-A.11OC_3 | 2701-PK-1501A-M_PERMIT.MCU | MCU.2701-PK-1501A-M - ITF Waste Gas FanAcoustic Enclosure Fan_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 217 | Read | BOOL | 02
219 | 2202-NK-SG-102-A.11OC_3 | 2701-PK-1501A-M_FAULT.MCU | MCU.2701-PK-1501A-M - ITF Waste Gas FanAcoustic Enclosure Fan_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 218 | Read | BOOL | 02
220 | 2202-NK-SG-102-A.11OC_3 | 2701-PK-1501A-M_STA.MCU | MCU.2701-PK-1501A-M - ITF Waste Gas FanAcoustic Enclosure Fan_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 219 | Read | BOOL | 02
221 | 2202-NK-SG-102-A.11OC_3 | 2701-PK-1501A-M_EM_STOP.MCU | MCU.2701-PK-1501A-M - ITF Waste Gas FanAcoustic Enclosure Fan_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 220 | Read | BOOL | 02
222 | 2202-NK-SG-102-A.11OC_3 | 2701-PK-1501A-M_SWITCH_ON.MCU | MCU.2701-PK-1501A-M - ITF Waste Gas FanAcoustic Enclosure Fan_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 221 | Read | BOOL | 02
223 | 2202-NK-SG-102-A.11OC_3 | 2701-PK-1501A-M_MCCB POSITION.MCU | MCU.2701-PK-1501A-M - ITF Waste Gas FanAcoustic Enclosure Fan_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 222 | Read | BOOL | 02
224 | 2202-NK-SG-102-A.11OC_3 | 2701-PK-1501A-M_REDAY.MCU | MCU.2701-PK-1501A-M - ITF Waste Gas FanAcoustic Enclosure Fan_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 223 | Read | BOOL | 02
225 | 2202-NK-SG-102-A.11OC_4 | 2701-PM-1215_TX.MCU | MCU.2701-PM-1215 - Slop Drum HC Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 224 | Read | BOOL | 02
226 | 2202-NK-SG-102-A.11OC_4 | 2701-PM-1215_PERMIT.MCU | MCU.2701-PM-1215 - Slop Drum HC Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 225 | Read | BOOL | 02
227 | 2202-NK-SG-102-A.11OC_4 | 2701-PM-1215_FAULT.MCU | MCU.2701-PM-1215 - Slop Drum HC Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 226 | Read | BOOL | 02
228 | 2202-NK-SG-102-A.11OC_4 | 2701-PM-1215_STA.MCU | MCU.2701-PM-1215 - Slop Drum HC Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 227 | Read | BOOL | 02
229 | 2202-NK-SG-102-A.11OC_4 | 2701-PM-1215_EM_STOP.MCU | MCU.2701-PM-1215 - Slop Drum HC Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 228 | Read | BOOL | 02
230 | 2202-NK-SG-102-A.11OC_4 | 2701-PM-1215_SWITCH_ON.MCU | MCU.2701-PM-1215 - Slop Drum HC Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 229 | Read | BOOL | 02
231 | 2202-NK-SG-102-A.11OC_4 | 2701-PM-1215_MCCB POSITION.MCU | MCU.2701-PM-1215 - Slop Drum HC Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 230 | Read | BOOL | 02
232 | 2202-NK-SG-102-A.11OC_4 | 2701-PM-1215_REDAY.MCU | MCU.2701-PM-1215 - Slop Drum HC Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 231 | Read | BOOL | 02
233 | 2202-NK-SG-102-A.11OC_5 | 2701-PM-1701A_TX.MCU | MCU.2701-PM-1701A - TBC Solution Dosing pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 232 | Read | BOOL | 02
234 | 2202-NK-SG-102-A.11OC_5 | 2701-PM-1701A_PERMIT.MCU | MCU.2701-PM-1701A - TBC Solution Dosing pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 233 | Read | BOOL | 02
235 | 2202-NK-SG-102-A.11OC_5 | 2701-PM-1701A_FAULT.MCU | MCU.2701-PM-1701A - TBC Solution Dosing pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 234 | Read | BOOL | 02
236 | 2202-NK-SG-102-A.11OC_5 | 2701-PM-1701A_STA.MCU | MCU.2701-PM-1701A - TBC Solution Dosing pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 235 | Read | BOOL | 02
237 | 2202-NK-SG-102-A.11OC_5 | 2701-PM-1701A_EM_STOP.MCU | MCU.2701-PM-1701A - TBC Solution Dosing pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 236 | Read | BOOL | 02
238 | 2202-NK-SG-102-A.11OC_5 | 2701-PM-1701A_SWITCH_ON.MCU | MCU.2701-PM-1701A - TBC Solution Dosing pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 237 | Read | BOOL | 02
239 | 2202-NK-SG-102-A.11OC_5 | 2701-PM-1701A_MCCB POSITION.MCU | MCU.2701-PM-1701A - TBC Solution Dosing pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 238 | Read | BOOL | 02
240 | 2202-NK-SG-102-A.11OC_5 | 2701-PM-1701A_REDAY.MCU | MCU.2701-PM-1701A - TBC Solution Dosing pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 239 | Read | BOOL | 02
241 | 2202-NK-SG-102-A.11OC_6 | 2701-AGM-1701_TX.MCU | MCU.2701-AGM-1701 - TBC Solution StorageDrum 2701-V-1701Agitator_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 240 | Read | BOOL | 02
242 | 2202-NK-SG-102-A.11OC_6 | 2701-AGM-1701_PERMIT.MCU | MCU.2701-AGM-1701 - TBC Solution StorageDrum 2701-V-1701Agitator_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 241 | Read | BOOL | 02
243 | 2202-NK-SG-102-A.11OC_6 | 2701-AGM-1701_FAULT.MCU | MCU.2701-AGM-1701 - TBC Solution StorageDrum 2701-V-1701Agitator_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 242 | Read | BOOL | 02
244 | 2202-NK-SG-102-A.11OC_6 | 2701-AGM-1701_STA.MCU | MCU.2701-AGM-1701 - TBC Solution StorageDrum 2701-V-1701Agitator_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 243 | Read | BOOL | 02
245 | 2202-NK-SG-102-A.11OC_6 | 2701-AGM-1701_EM_STOP.MCU | MCU.2701-AGM-1701 - TBC Solution StorageDrum 2701-V-1701Agitator_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 244 | Read | BOOL | 02
246 | 2202-NK-SG-102-A.11OC_6 | 2701-AGM-1701_SWITCH_ON.MCU | MCU.2701-AGM-1701 - TBC Solution StorageDrum 2701-V-1701Agitator_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 245 | Read | BOOL | 02
247 | 2202-NK-SG-102-A.11OC_6 | 2701-AGM-1701_MCCB POSITION.MCU | MCU.2701-AGM-1701 - TBC Solution StorageDrum 2701-V-1701Agitator_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 246 | Read | BOOL | 02
248 | 2202-NK-SG-102-A.11OC_6 | 2701-AGM-1701_REDAY.MCU | MCU.2701-AGM-1701 - TBC Solution StorageDrum 2701-V-1701Agitator_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 247 | Read | BOOL | 02
249 | 2202-NK-SG-102-A.11OC_7 | 2701-PM-1206A_TX.MCU | MCU.2701-PM-1206A - Benzene-Toluene FractionTransfer Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 248 | Read | BOOL | 02
250 | 2202-NK-SG-102-A.11OC_7 | 2701-PM-1206A_PERMIT.MCU | MCU.2701-PM-1206A - Benzene-Toluene FractionTransfer Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 249 | Read | BOOL | 02
251 | 2202-NK-SG-102-A.11OC_7 | 2701-PM-1206A_FAULT.MCU | MCU.2701-PM-1206A - Benzene-Toluene FractionTransfer Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 250 | Read | BOOL | 02
252 | 2202-NK-SG-102-A.11OC_7 | 2701-PM-1206A_STA.MCU | MCU.2701-PM-1206A - Benzene-Toluene FractionTransfer Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 251 | Read | BOOL | 02
253 | 2202-NK-SG-102-A.11OC_7 | 2701-PM-1206A_EM_STOP.MCU | MCU.2701-PM-1206A - Benzene-Toluene FractionTransfer Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 252 | Read | BOOL | 02
254 | 2202-NK-SG-102-A.11OC_7 | 2701-PM-1206A_SWITCH_ON.MCU | MCU.2701-PM-1206A - Benzene-Toluene FractionTransfer Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 253 | Read | BOOL | 02
255 | 2202-NK-SG-102-A.11OC_7 | 2701-PM-1206A_MCCB POSITION.MCU | MCU.2701-PM-1206A - Benzene-Toluene FractionTransfer Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 254 | Read | BOOL | 02
256 | 2202-NK-SG-102-A.11OC_7 | 2701-PM-1206A_REDAY.MCU | MCU.2701-PM-1206A - Benzene-Toluene FractionTransfer Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 255 | Read | BOOL | 02
257 | 2202-NK-SG-102-A.11OC_8 | 2202-NK-SG-102-A.11OC_8_TX.MCU | MCU.2202-NK-SG-102-A.11OC_8 - SPARE_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 256 | Read | BOOL | 02
258 | 2202-NK-SG-102-A.11OC_8 | 2202-NK-SG-102-A.11OC_8_PERMIT.MCU | MCU.2202-NK-SG-102-A.11OC_8 - SPARE_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 257 | Read | BOOL | 02
259 | 2202-NK-SG-102-A.11OC_8 | 2202-NK-SG-102-A.11OC_8_FAULT.MCU | MCU.2202-NK-SG-102-A.11OC_8 - SPARE_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 258 | Read | BOOL | 02
260 | 2202-NK-SG-102-A.11OC_8 | 2202-NK-SG-102-A.11OC_8_STA.MCU | MCU.2202-NK-SG-102-A.11OC_8 - SPARE_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 259 | Read | BOOL | 02
261 | 2202-NK-SG-102-A.11OC_8 | 2202-NK-SG-102-A.11OC_8_EM_STOP.MCU | MCU.2202-NK-SG-102-A.11OC_8 - SPARE_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 260 | Read | BOOL | 02
262 | 2202-NK-SG-102-A.11OC_8 | 2202-NK-SG-102-A.11OC_8_SWITCH_ON.MCU | MCU.2202-NK-SG-102-A.11OC_8 - SPARE_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 261 | Read | BOOL | 02
263 | 2202-NK-SG-102-A.11OC_8 | 2202-NK-SG-102-A.11OC_8_MCCB POSITION.MCU | MCU.2202-NK-SG-102-A.11OC_8 - SPARE_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 262 | Read | BOOL | 02
264 | 2202-NK-SG-102-A.11OC_8 | 2202-NK-SG-102-A.11OC_8_REDAY.MCU | MCU.2202-NK-SG-102-A.11OC_8 - SPARE_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 263 | Read | BOOL | 02
265 | 2202-NK-SG-102-A.15OC_1 | 1130-PM-301A_TX.MCU | MCU.1130-PM-301A - DM Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 264 | Read | BOOL | 02
266 | 2202-NK-SG-102-A.15OC_1 | 1130-PM-301A_EM_STOP.MCU | MCU.1130-PM-301A - DM Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 265 | Read | BOOL | 02
267 | 2202-NK-SG-102-A.15OC_2 | 1130-PM-303A_TX.MCU | MCU.1130-PM-303A - Condensate Stripper Bottom Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 266 | Read | BOOL | 02
268 | 2202-NK-SG-102-A.15OC_2 | 1130-PM-303A_EM_STOP.MCU | MCU.1130-PM-303A - Condensate Stripper Bottom Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 267 | Read | BOOL | 02
269 | 2202-NK-SG-102-A.15OC_3 | 1612-PM-606A_TX.MCU | MCU.1612-PM-606A - LLP Condensate Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 268 | Read | BOOL | 02
270 | 2202-NK-SG-102-A.15OC_3 | 1612-PM-606A_EM_STOP.MCU | MCU.1612-PM-606A - LLP Condensate Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 269 | Read | BOOL | 02
271 | 2202-NK-SG-102-A.17OC_1 | 2701-PM-1202A_TX.MCU | MCU.2701-PM-1202A - Ethylbenzene transfer pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 270 | Read | BOOL | 02
272 | 2202-NK-SG-102-A.17OC_1 | 2701-PM-1202A_EM_STOP.MCU | MCU.2701-PM-1202A - Ethylbenzene transfer pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 271 | Read | BOOL | 02
273 | 2202-NK-SG-102-A.17OC_2 | 2701-PM-1201A_TX.MCU | MCU.2701-PM-1201A - Benzene transfer pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 272 | Read | BOOL | 02
274 | 2202-NK-SG-102-A.17OC_2 | 2701-PM-1201A_EM_STOP.MCU | MCU.2701-PM-1201A - Benzene transfer pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 273 | Read | BOOL | 02
275 | 2202-NK-SG-102-A.17OC_3 | 2701-PM-1204A_TX.MCU | MCU.2701-PM-1204A - DM Transfer Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 274 | Read | BOOL | 02
276 | 2202-NK-SG-102-A.17OC_3 | 2701-PM-1204A_EM_STOP.MCU | MCU.2701-PM-1204A - DM Transfer Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 275 | Read | BOOL | 02
277 | 2202-NK-SG-102-A.19OC_1 | 2701-PM-1203_TX.MCU | MCU.2701-PM-1203 - Off-Spec EB Transfer Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 276 | Read | BOOL | 02
278 | 2202-NK-SG-102-A.19OC_1 | 2701-PM-1203_EM_STOP.MCU | MCU.2701-PM-1203 - Off-Spec EB Transfer Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 277 | Read | BOOL | 02
279 | 2202-NK-SG-102-A.19OC_2 | 2701-PM-1207A_TX.MCU | MCU.2701-PM-1207A - Heavy Tar Loading Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 278 | Read | BOOL | 02
280 | 2202-NK-SG-102-A.19OC_2 | 2701-PM-1207A_EM_STOP.MCU | MCU.2701-PM-1207A - Heavy Tar Loading Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 279 | Read | BOOL | 02
281 | 2202-NK-SG-102-A.19OC_3 | 2701-PM-1205B_TX.MCU | MCU.2701-PM-1205B - SM Transfer Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 280 | Read | BOOL | 02
282 | 2202-NK-SG-102-A.19OC_3 | 2701-PM-1205B_EM_STOP.MCU | MCU.2701-PM-1205B - SM Transfer Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 281 | Read | BOOL | 02
283 | 2202-NK-SG-102-A.SS01_1 | 2202-NK-SG-102-A.SS01_1_PLC_TX.PLC | PLC.2202-NK-SG-102-A.SS01_1 - inlet switch+SOFT STARTER_SSR PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  | SSR PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 282 | Read | BOOL | 02
284 | 2202-NK-SG-102-A.SS01_1 | 1130-PM-301A_M1_PERMIT.PLC | PLC.1130-PM-301A - DM Pump_Circuit 1_Permitted State 1:Permit 0:Not Permit |  | Circuit 1_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 283 | Read | BOOL | 02
285 | 2202-NK-SG-102-A.SS01_1 | 1130-PM-301A_Q1_READY.PLC | PLC.1130-PM-301A - DM Pump_Circuit 1_Q1_Ready 1:Ready 0:Not Ready |  | Circuit 1_Q1_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 284 | Read | BOOL | 02
286 | 2202-NK-SG-102-A.SS01_1 | 1130-PM-301A_Q1_BYPS.PLC | PLC.1130-PM-301A - DM Pump_Circuit 1_Q1_Motor 1 Operation 1:Running 0:Stopped |  | Circuit 1_Q1_Motor 1 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 285 | Read | BOOL | 02
287 | 2202-NK-SG-102-A.SS01_1 | 1130-PM-301A_Q1_F.PLC | PLC.1130-PM-301A - DM Pump_Circuit 1_Q1_Motor 1 Fault 1:Fault 0:Normal |  | Circuit 1_Q1_Motor 1 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 286 | Read | BOOL | 02
288 | 2202-NK-SG-102-A.SS01_1 | 1130-PM-301A_QF1_ATUO.PLC | PLC.1130-PM-301A - DM Pump_Circuit 1_Q1_Remote_Local 1:Remote 0:Local |  | Circuit 1_Q1_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 287 | Read | BOOL | 02
289 | 2202-NK-SG-102-A.SS01_1 | 1130-PM-301A_QF1_STA.PLC | PLC.1130-PM-301A - DM Pump_Circuit 1_QF1_Switch Closing 1:Closed 0:Open |  | Circuit 1_QF1_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 288 | Read | BOOL | 02
290 | 2202-NK-SG-102-A.SS01_1 | 1130-PM-303A_M2_PERMIT.PLC | PLC.1130-PM-303A - Condensate Stripper Bottom Pump_Circuit 2_Permitted State 1:Permit 0:Not Permit |  | Circuit 2_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 289 | Read | BOOL | 02
291 | 2202-NK-SG-102-A.SS01_1 | 1130-PM-303A_Q2_READY.PLC | PLC.1130-PM-303A - Condensate Stripper Bottom Pump_Circuit 2_Q2_Ready 1:Ready 0:Not Ready |  | Circuit 2_Q2_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 290 | Read | BOOL | 02
292 | 2202-NK-SG-102-A.SS01_1 | 1130-PM-303A_Q2_BYPS.PLC | PLC.1130-PM-303A - Condensate Stripper Bottom Pump_Circuit 2_Q2_Motor 2 Operation 1:Running 0:Stopped |  | Circuit 2_Q2_Motor 2 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 291 | Read | BOOL | 02
293 | 2202-NK-SG-102-A.SS01_1 | 1130-PM-303A_Q2_F.PLC | PLC.1130-PM-303A - Condensate Stripper Bottom Pump_Circuit 2_Q2_Motor 2 Fault 1:Fault 0:Normal |  | Circuit 2_Q2_Motor 2 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 292 | Read | BOOL | 02
294 | 2202-NK-SG-102-A.SS01_1 | 1130-PM-303A_QF2_ATUO.PLC | PLC.1130-PM-303A - Condensate Stripper Bottom Pump_Circuit 2_Q2_Remote_Local 1:Remote 0:Local |  | Circuit 2_Q2_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 293 | Read | BOOL | 02
295 | 2202-NK-SG-102-A.SS01_1 | 1130-PM-303A_QF2_STA.PLC | PLC.1130-PM-303A - Condensate Stripper Bottom Pump_Circuit 2_QF2_Switch Closing 1:Closed 0:Open |  | Circuit 2_QF2_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 294 | Read | BOOL | 02
296 | 2202-NK-SG-102-A.SS01_1 | 1612-PM-606A_M3_PERMIT.PLC | PLC.1612-PM-606A - LLP Condensate Pump_Circuit 3_Permitted State 1:Permit 0:Not Permit |  | Circuit 3_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 295 | Read | BOOL | 02
297 | 2202-NK-SG-102-A.SS01_1 | 1612-PM-606A_Q3_READY.PLC | PLC.1612-PM-606A - LLP Condensate Pump_Circuit 3_Q3_Ready 1:Ready 0:Not Ready |  | Circuit 3_Q3_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 296 | Read | BOOL | 02
298 | 2202-NK-SG-102-A.SS01_1 | 1612-PM-606A_Q3_BYPS.PLC | PLC.1612-PM-606A - LLP Condensate Pump_Circuit 3_Q3_Motor 3 Operation 1:Running 0:Stopped |  | Circuit 3_Q3_Motor 3 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 297 | Read | BOOL | 02
299 | 2202-NK-SG-102-A.SS01_1 | 1612-PM-606A_Q3_F.PLC | PLC.1612-PM-606A - LLP Condensate Pump_Circuit 3_Q3_Motor 3 Fault 1:Fault 0:Normal |  | Circuit 3_Q3_Motor 3 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 298 | Read | BOOL | 02
300 | 2202-NK-SG-102-A.SS01_1 | 1612-PM-606A_QF3_ATUO.PLC | PLC.1612-PM-606A - LLP Condensate Pump_Circuit 3_Q3_Remote_Local 1:Remote 0:Local |  | Circuit 3_Q3_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 299 | Read | BOOL | 02
301 | 2202-NK-SG-102-A.SS01_1 | 1612-PM-606A_QF3_STA.PLC | PLC.1612-PM-606A - LLP Condensate Pump_Circuit 3_QF3_Switch Closing 1:Closed 0:Open |  | Circuit 3_QF3_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 300 | Read | BOOL | 02
302 | 2202-NK-SG-102-A.SS03_1 | 2202-NK-SG-102-A.SS03_1_PLC_TX.PLC | PLC.2202-NK-SG-102-A.SS03_1 - inlet switch+SOFT STARTER_SSR PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  | SSR PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 301 | Read | BOOL | 02
303 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1202A_M1_PERMIT.PLC | PLC.2701-PM-1202A - Ethylbenzene transfer pump_Circuit 1_Permitted State 1:Permit 0:Not Permit |  | Circuit 1_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 302 | Read | BOOL | 02
304 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1202A_Q1_READY.PLC | PLC.2701-PM-1202A - Ethylbenzene transfer pump_Circuit 1_Q1_Ready 1:Ready 0:Not Ready |  | Circuit 1_Q1_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 303 | Read | BOOL | 02
305 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1202A_Q1_BYPS.PLC | PLC.2701-PM-1202A - Ethylbenzene transfer pump_Circuit 1_Q1_Motor 1 Operation 1:Running 0:Stopped |  | Circuit 1_Q1_Motor 1 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 304 | Read | BOOL | 02
306 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1202A_Q1_F.PLC | PLC.2701-PM-1202A - Ethylbenzene transfer pump_Circuit 1_Q1_Motor 1 Fault 1:Fault 0:Normal |  | Circuit 1_Q1_Motor 1 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 305 | Read | BOOL | 02
307 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1202A_QF1_ATUO.PLC | PLC.2701-PM-1202A - Ethylbenzene transfer pump_Circuit 1_Q1_Remote_Local 1:Remote 0:Local |  | Circuit 1_Q1_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 306 | Read | BOOL | 02
308 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1202A_QF1_STA.PLC | PLC.2701-PM-1202A - Ethylbenzene transfer pump_Circuit 1_QF1_Switch Closing 1:Closed 0:Open |  | Circuit 1_QF1_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 307 | Read | BOOL | 02
309 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1201A_M2_PERMIT.PLC | PLC.2701-PM-1201A - Benzene transfer pump_Circuit 2_Permitted State 1:Permit 0:Not Permit |  | Circuit 2_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 308 | Read | BOOL | 02
310 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1201A_Q2_READY.PLC | PLC.2701-PM-1201A - Benzene transfer pump_Circuit 2_Q2_Ready 1:Ready 0:Not Ready |  | Circuit 2_Q2_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 309 | Read | BOOL | 02
311 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1201A_Q2_BYPS.PLC | PLC.2701-PM-1201A - Benzene transfer pump_Circuit 2_Q2_Motor 2 Operation 1:Running 0:Stopped |  | Circuit 2_Q2_Motor 2 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 310 | Read | BOOL | 02
312 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1201A_Q2_F.PLC | PLC.2701-PM-1201A - Benzene transfer pump_Circuit 2_Q2_Motor 2 Fault 1:Fault 0:Normal |  | Circuit 2_Q2_Motor 2 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 311 | Read | BOOL | 02
313 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1201A_QF2_ATUO.PLC | PLC.2701-PM-1201A - Benzene transfer pump_Circuit 2_Q2_Remote_Local 1:Remote 0:Local |  | Circuit 2_Q2_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 312 | Read | BOOL | 02
314 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1201A_QF2_STA.PLC | PLC.2701-PM-1201A - Benzene transfer pump_Circuit 2_QF2_Switch Closing 1:Closed 0:Open |  | Circuit 2_QF2_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 313 | Read | BOOL | 02
315 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1204A_M3_PERMIT.PLC | PLC.2701-PM-1204A - DM Transfer Pump_Circuit 3_Permitted State 1:Permit 0:Not Permit |  | Circuit 3_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 314 | Read | BOOL | 02
316 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1204A_Q3_READY.PLC | PLC.2701-PM-1204A - DM Transfer Pump_Circuit 3_Q3_Ready 1:Ready 0:Not Ready |  | Circuit 3_Q3_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 315 | Read | BOOL | 02
317 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1204A_Q3_BYPS.PLC | PLC.2701-PM-1204A - DM Transfer Pump_Circuit 3_Q3_Motor 3 Operation 1:Running 0:Stopped |  | Circuit 3_Q3_Motor 3 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 316 | Read | BOOL | 02
318 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1204A_Q3_F.PLC | PLC.2701-PM-1204A - DM Transfer Pump_Circuit 3_Q3_Motor 3 Fault 1:Fault 0:Normal |  | Circuit 3_Q3_Motor 3 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 317 | Read | BOOL | 02
319 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1204A_QF3_ATUO.PLC | PLC.2701-PM-1204A - DM Transfer Pump_Circuit 3_Q3_Remote_Local 1:Remote 0:Local |  | Circuit 3_Q3_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 318 | Read | BOOL | 02
320 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1204A_QF3_STA.PLC | PLC.2701-PM-1204A - DM Transfer Pump_Circuit 3_QF3_Switch Closing 1:Closed 0:Open |  | Circuit 3_QF3_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 319 | Read | BOOL | 02
321 | 2202-NK-SG-102-A.SS05_1 | 2202-NK-SG-102-A.SS05_1_PLC_TX.PLC | PLC.2202-NK-SG-102-A.SS05_1 - inlet switch+SOFT STARTER_SSR PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  | SSR PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 320 | Read | BOOL | 02
322 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1203_M1_PERMIT.PLC | PLC.2701-PM-1203 - Off-Spec EB Transfer Pump_Circuit 1_Permitted State 1:Permit 0:Not Permit |  | Circuit 1_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 321 | Read | BOOL | 02
323 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1203_Q1_READY.PLC | PLC.2701-PM-1203 - Off-Spec EB Transfer Pump_Circuit 1_Q1_Ready 1:Ready 0:Not Ready |  | Circuit 1_Q1_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 322 | Read | BOOL | 02
324 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1203_Q1_BYPS.PLC | PLC.2701-PM-1203 - Off-Spec EB Transfer Pump_Circuit 1_Q1_Motor 1 Operation 1:Running 0:Stopped |  | Circuit 1_Q1_Motor 1 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 323 | Read | BOOL | 02
325 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1203_Q1_F.PLC | PLC.2701-PM-1203 - Off-Spec EB Transfer Pump_Circuit 1_Q1_Motor 1 Fault 1:Fault 0:Normal |  | Circuit 1_Q1_Motor 1 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 324 | Read | BOOL | 02
326 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1203_QF1_ATUO.PLC | PLC.2701-PM-1203 - Off-Spec EB Transfer Pump_Circuit 1_Q1_Remote_Local 1:Remote 0:Local |  | Circuit 1_Q1_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 325 | Read | BOOL | 02
327 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1203_QF1_STA.PLC | PLC.2701-PM-1203 - Off-Spec EB Transfer Pump_Circuit 1_QF1_Switch Closing 1:Closed 0:Open |  | Circuit 1_QF1_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 326 | Read | BOOL | 02
328 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1207A_M2_PERMIT.PLC | PLC.2701-PM-1207A - Heavy Tar Loading Pump_Circuit 2_Permitted State 1:Permit 0:Not Permit |  | Circuit 2_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 327 | Read | BOOL | 02
329 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1207A_Q2_READY.PLC | PLC.2701-PM-1207A - Heavy Tar Loading Pump_Circuit 2_Q2_Ready 1:Ready 0:Not Ready |  | Circuit 2_Q2_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 328 | Read | BOOL | 02
330 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1207A_Q2_BYPS.PLC | PLC.2701-PM-1207A - Heavy Tar Loading Pump_Circuit 2_Q2_Motor 2 Operation 1:Running 0:Stopped |  | Circuit 2_Q2_Motor 2 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 329 | Read | BOOL | 02
331 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1207A_Q2_F.PLC | PLC.2701-PM-1207A - Heavy Tar Loading Pump_Circuit 2_Q2_Motor 2 Fault 1:Fault 0:Normal |  | Circuit 2_Q2_Motor 2 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 330 | Read | BOOL | 02
332 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1207A_QF2_ATUO.PLC | PLC.2701-PM-1207A - Heavy Tar Loading Pump_Circuit 2_Q2_Remote_Local 1:Remote 0:Local |  | Circuit 2_Q2_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 331 | Read | BOOL | 02
333 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1207A_QF2_STA.PLC | PLC.2701-PM-1207A - Heavy Tar Loading Pump_Circuit 2_QF2_Switch Closing 1:Closed 0:Open |  | Circuit 2_QF2_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 332 | Read | BOOL | 02
334 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1205B_M3_PERMIT.PLC | PLC.2701-PM-1205B - SM Transfer Pump_Circuit 3_Permitted State 1:Permit 0:Not Permit |  | Circuit 3_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 333 | Read | BOOL | 02
335 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1205B_Q3_READY.PLC | PLC.2701-PM-1205B - SM Transfer Pump_Circuit 3_Q3_Ready 1:Ready 0:Not Ready |  | Circuit 3_Q3_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 334 | Read | BOOL | 02
336 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1205B_Q3_BYPS.PLC | PLC.2701-PM-1205B - SM Transfer Pump_Circuit 3_Q3_Motor 3 Operation 1:Running 0:Stopped |  | Circuit 3_Q3_Motor 3 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 335 | Read | BOOL | 02
337 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1205B_Q3_F.PLC | PLC.2701-PM-1205B - SM Transfer Pump_Circuit 3_Q3_Motor 3 Fault 1:Fault 0:Normal |  | Circuit 3_Q3_Motor 3 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 336 | Read | BOOL | 02
338 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1205B_QF3_ATUO.PLC | PLC.2701-PM-1205B - SM Transfer Pump_Circuit 3_Q3_Remote_Local 1:Remote 0:Local |  | Circuit 3_Q3_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 337 | Read | BOOL | 02
339 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1205B_QF3_STA.PLC | PLC.2701-PM-1205B - SM Transfer Pump_Circuit 3_QF3_Switch Closing 1:Closed 0:Open |  | Circuit 3_QF3_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 338 | Read | BOOL | 02
340 | 2202-NK-SG-102-A.23OC_1 | 2701-PK-1201A-M_TX.VFD | VFD.2701-PK-1201A-M - ITF Waste Gas Fan_VFD Communication Status 1:Communication Normal 0:Communication Interrupted |  | VFD Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 339 | Read | BOOL | 02
341 | 2202-NK-SG-102-A.23OC_1 | 2701-PK-1201A-M_TX.PLC | PLC.2701-PK-1201A-M - ITF Waste Gas Fan_VFD PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  | VFD PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 340 | Read | BOOL | 02
342 | 2202-NK-SG-102-A.23OC_1 | 2701-PK-1201A-M_PERMIT.PLC | PLC.2701-PK-1201A-M - ITF Waste Gas Fan_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 341 | Read | BOOL | 02
343 | 2202-NK-SG-102-A.23OC_1 | 2701-PK-1201A-M_LOC_REM.PLC | PLC.2701-PK-1201A-M - ITF Waste Gas Fan_Remote_Local 1:Remote 0:Local |  | Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 342 | Read | BOOL | 02
344 | 2202-NK-SG-102-A.23OC_1 | 2701-PK-1201A-M_STA.PLC | PLC.2701-PK-1201A-M - ITF Waste Gas Fan_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 343 | Read | BOOL | 02
345 | 2202-NK-SG-102-A.23OC_1 | 2701-PK-1201A-M_REDAY.PLC | PLC.2701-PK-1201A-M - ITF Waste Gas Fan_Motor ALLReady 1:Ready 0:Not Ready |  | Motor ALLReady 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 344 | Read | BOOL | 02
346 | 2202-NK-SG-102-A.23OC_1 | 2701-PK-1201A-M_SWITCH_ON.PLC | PLC.2701-PK-1201A-M - ITF Waste Gas Fan_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 345 | Read | BOOL | 02
347 | 2202-NK-SG-102-A.23OC_1 | 2701-PK-1201A-M_DOORSTA.PLC | PLC.2701-PK-1201A-M - ITF Waste Gas Fan_Cabinet Door Closed 1:Cabinet Door Closed 0:Open |  | Cabinet Door Closed 1:Cabinet Door Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 346 | Read | BOOL | 02
348 | 2202-NK-SG-102-A.23OC_1 | 2701-PK-1201A-M_FAULT.PLC | PLC.2701-PK-1201A-M - ITF Waste Gas Fan_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 347 | Read | BOOL | 02
349 | 2202-NK-SG-102-A.23OC_1 | 2701-PK-1201A-M_EM_STOP.PLC | PLC.2701-PK-1201A-M - ITF Waste Gas Fan_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 348 | Read | BOOL | 02
350 | 2202-NK-SG-102-B.06OC_1 | 1115-PM-101B_TX.MCU | MCU.1115-PM-101B - R-101 Recycle Pumps_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 349 | Read | BOOL | 02
351 | 2202-NK-SG-102-B.06OC_1 | 1115-PM-101B_PERMIT.MCU | MCU.1115-PM-101B - R-101 Recycle Pumps_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 350 | Read | BOOL | 02
352 | 2202-NK-SG-102-B.06OC_1 | 1115-PM-101B_FAULT.MCU | MCU.1115-PM-101B - R-101 Recycle Pumps_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 351 | Read | BOOL | 02
353 | 2202-NK-SG-102-B.06OC_1 | 1115-PM-101B_STA.MCU | MCU.1115-PM-101B - R-101 Recycle Pumps_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 352 | Read | BOOL | 02
354 | 2202-NK-SG-102-B.06OC_1 | 1115-PM-101B_EM_STOP.MCU | MCU.1115-PM-101B - R-101 Recycle Pumps_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 353 | Read | BOOL | 02
355 | 2202-NK-SG-102-B.06OC_1 | 1115-PM-101B_SWITCH_ON.MCU | MCU.1115-PM-101B - R-101 Recycle Pumps_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 354 | Read | BOOL | 02
356 | 2202-NK-SG-102-B.06OC_1 | 1115-PM-101B_MCCB POSITION.MCU | MCU.1115-PM-101B - R-101 Recycle Pumps_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 355 | Read | BOOL | 02
357 | 2202-NK-SG-102-B.06OC_1 | 1115-PM-101B_REDAY.MCU | MCU.1115-PM-101B - R-101 Recycle Pumps_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 356 | Read | BOOL | 02
358 | 2202-NK-SG-102-B.06OC_2 | 1630-PM-214B_TX.MCU | MCU.1630-PM-214B - HP Flare K.O.Drum Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 357 | Read | BOOL | 02
359 | 2202-NK-SG-102-B.06OC_2 | 1630-PM-214B_PERMIT.MCU | MCU.1630-PM-214B - HP Flare K.O.Drum Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 358 | Read | BOOL | 02
360 | 2202-NK-SG-102-B.06OC_2 | 1630-PM-214B_FAULT.MCU | MCU.1630-PM-214B - HP Flare K.O.Drum Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 359 | Read | BOOL | 02
361 | 2202-NK-SG-102-B.06OC_2 | 1630-PM-214B_STA.MCU | MCU.1630-PM-214B - HP Flare K.O.Drum Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 360 | Read | BOOL | 02
362 | 2202-NK-SG-102-B.06OC_2 | 1630-PM-214B_EM_STOP.MCU | MCU.1630-PM-214B - HP Flare K.O.Drum Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 361 | Read | BOOL | 02
363 | 2202-NK-SG-102-B.06OC_2 | 1630-PM-214B_SWITCH_ON.MCU | MCU.1630-PM-214B - HP Flare K.O.Drum Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 362 | Read | BOOL | 02
364 | 2202-NK-SG-102-B.06OC_2 | 1630-PM-214B_MCCB POSITION.MCU | MCU.1630-PM-214B - HP Flare K.O.Drum Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 363 | Read | BOOL | 02
365 | 2202-NK-SG-102-B.06OC_2 | 1630-PM-214B_REDAY.MCU | MCU.1630-PM-214B - HP Flare K.O.Drum Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 364 | Read | BOOL | 02
366 | 2202-NK-SG-102-B.06OC_3 | 1630-PM-605B_TX.MCU | MCU.1630-PM-605B - LP Flare K.O.Drum Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 365 | Read | BOOL | 02
367 | 2202-NK-SG-102-B.06OC_3 | 1630-PM-605B_PERMIT.MCU | MCU.1630-PM-605B - LP Flare K.O.Drum Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 366 | Read | BOOL | 02
368 | 2202-NK-SG-102-B.06OC_3 | 1630-PM-605B_FAULT.MCU | MCU.1630-PM-605B - LP Flare K.O.Drum Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 367 | Read | BOOL | 02
369 | 2202-NK-SG-102-B.06OC_3 | 1630-PM-605B_STA.MCU | MCU.1630-PM-605B - LP Flare K.O.Drum Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 368 | Read | BOOL | 02
370 | 2202-NK-SG-102-B.06OC_3 | 1630-PM-605B_EM_STOP.MCU | MCU.1630-PM-605B - LP Flare K.O.Drum Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 369 | Read | BOOL | 02
371 | 2202-NK-SG-102-B.06OC_3 | 1630-PM-605B_SWITCH_ON.MCU | MCU.1630-PM-605B - LP Flare K.O.Drum Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 370 | Read | BOOL | 02
372 | 2202-NK-SG-102-B.06OC_3 | 1630-PM-605B_MCCB POSITION.MCU | MCU.1630-PM-605B - LP Flare K.O.Drum Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 371 | Read | BOOL | 02
373 | 2202-NK-SG-102-B.06OC_3 | 1630-PM-605B_REDAY.MCU | MCU.1630-PM-605B - LP Flare K.O.Drum Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 372 | Read | BOOL | 02
374 | 2202-NK-SG-102-B.06OC_4 | 1130-PM-305B_TX.MCU | MCU.1130-PM-305B - Offgas Absorber Bottom Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 373 | Read | BOOL | 02
375 | 2202-NK-SG-102-B.06OC_4 | 1130-PM-305B_PERMIT.MCU | MCU.1130-PM-305B - Offgas Absorber Bottom Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 374 | Read | BOOL | 02
376 | 2202-NK-SG-102-B.06OC_4 | 1130-PM-305B_FAULT.MCU | MCU.1130-PM-305B - Offgas Absorber Bottom Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 375 | Read | BOOL | 02
377 | 2202-NK-SG-102-B.06OC_4 | 1130-PM-305B_STA.MCU | MCU.1130-PM-305B - Offgas Absorber Bottom Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 376 | Read | BOOL | 02
378 | 2202-NK-SG-102-B.06OC_4 | 1130-PM-305B_EM_STOP.MCU | MCU.1130-PM-305B - Offgas Absorber Bottom Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 377 | Read | BOOL | 02
379 | 2202-NK-SG-102-B.06OC_4 | 1130-PM-305B_SWITCH_ON.MCU | MCU.1130-PM-305B - Offgas Absorber Bottom Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 378 | Read | BOOL | 02
380 | 2202-NK-SG-102-B.06OC_4 | 1130-PM-305B_MCCB POSITION.MCU | MCU.1130-PM-305B - Offgas Absorber Bottom Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 379 | Read | BOOL | 02
381 | 2202-NK-SG-102-B.06OC_4 | 1130-PM-305B_REDAY.MCU | MCU.1130-PM-305B - Offgas Absorber Bottom Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 380 | Read | BOOL | 02
382 | 2202-NK-SG-102-B.06OC_5 | 1130-PM-306B_TX.MCU | MCU.1130-PM-306B - Rich Oil Stripper Bottom Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 381 | Read | BOOL | 02
383 | 2202-NK-SG-102-B.06OC_5 | 1130-PM-306B_PERMIT.MCU | MCU.1130-PM-306B - Rich Oil Stripper Bottom Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 382 | Read | BOOL | 02
384 | 2202-NK-SG-102-B.06OC_5 | 1130-PM-306B_FAULT.MCU | MCU.1130-PM-306B - Rich Oil Stripper Bottom Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 383 | Read | BOOL | 02
385 | 2202-NK-SG-102-B.06OC_5 | 1130-PM-306B_STA.MCU | MCU.1130-PM-306B - Rich Oil Stripper Bottom Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 384 | Read | BOOL | 02
386 | 2202-NK-SG-102-B.06OC_5 | 1130-PM-306B_EM_STOP.MCU | MCU.1130-PM-306B - Rich Oil Stripper Bottom Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 385 | Read | BOOL | 02
387 | 2202-NK-SG-102-B.06OC_5 | 1130-PM-306B_SWITCH_ON.MCU | MCU.1130-PM-306B - Rich Oil Stripper Bottom Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 386 | Read | BOOL | 02
388 | 2202-NK-SG-102-B.06OC_5 | 1130-PM-306B_MCCB POSITION.MCU | MCU.1130-PM-306B - Rich Oil Stripper Bottom Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 387 | Read | BOOL | 02
389 | 2202-NK-SG-102-B.06OC_5 | 1130-PM-306B_REDAY.MCU | MCU.1130-PM-306B - Rich Oil Stripper Bottom Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 388 | Read | BOOL | 02
390 | 2202-NK-SG-102-B.06OC_6 | 1130-BLM-331B_TX.MCU | MCU.1130-BLM-331B - Oil station fans_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 389 | Read | BOOL | 02
391 | 2202-NK-SG-102-B.06OC_6 | 1130-BLM-331B_PERMIT.MCU | MCU.1130-BLM-331B - Oil station fans_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 390 | Read | BOOL | 02
392 | 2202-NK-SG-102-B.06OC_6 | 1130-BLM-331B_FAULT.MCU | MCU.1130-BLM-331B - Oil station fans_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 391 | Read | BOOL | 02
393 | 2202-NK-SG-102-B.06OC_6 | 1130-BLM-331B_STA.MCU | MCU.1130-BLM-331B - Oil station fans_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 392 | Read | BOOL | 02
394 | 2202-NK-SG-102-B.06OC_6 | 1130-BLM-331B_EM_STOP.MCU | MCU.1130-BLM-331B - Oil station fans_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 393 | Read | BOOL | 02
395 | 2202-NK-SG-102-B.06OC_6 | 1130-BLM-331B_SWITCH_ON.MCU | MCU.1130-BLM-331B - Oil station fans_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 394 | Read | BOOL | 02
396 | 2202-NK-SG-102-B.06OC_6 | 1130-BLM-331B_MCCB POSITION.MCU | MCU.1130-BLM-331B - Oil station fans_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 395 | Read | BOOL | 02
397 | 2202-NK-SG-102-B.06OC_6 | 1130-BLM-331B_REDAY.MCU | MCU.1130-BLM-331B - Oil station fans_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 396 | Read | BOOL | 02
398 | 2202-NK-SG-102-B.06OC_7 | 1130-PM-302B_TX.MCU | MCU.1130-PM-302B - Process Condensate Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 397 | Read | BOOL | 02
399 | 2202-NK-SG-102-B.06OC_7 | 1130-PM-302B_PERMIT.MCU | MCU.1130-PM-302B - Process Condensate Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 398 | Read | BOOL | 02
400 | 2202-NK-SG-102-B.06OC_7 | 1130-PM-302B_FAULT.MCU | MCU.1130-PM-302B - Process Condensate Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 399 | Read | BOOL | 02
401 | 2202-NK-SG-102-B.06OC_7 | 1130-PM-302B_STA.MCU | MCU.1130-PM-302B - Process Condensate Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 400 | Read | BOOL | 02
402 | 2202-NK-SG-102-B.06OC_7 | 1130-PM-302B_EM_STOP.MCU | MCU.1130-PM-302B - Process Condensate Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 401 | Read | BOOL | 02
403 | 2202-NK-SG-102-B.06OC_7 | 1130-PM-302B_SWITCH_ON.MCU | MCU.1130-PM-302B - Process Condensate Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 402 | Read | BOOL | 02
404 | 2202-NK-SG-102-B.06OC_7 | 1130-PM-302B_MCCB POSITION.MCU | MCU.1130-PM-302B - Process Condensate Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 403 | Read | BOOL | 02
405 | 2202-NK-SG-102-B.06OC_7 | 1130-PM-302B_REDAY.MCU | MCU.1130-PM-302B - Process Condensate Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 404 | Read | BOOL | 02
406 | 2202-NK-SG-102-B.08OC_1 | 1612-PM-611B_TX.MCU | MCU.1612-PM-611B - Desuperheater Water Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 405 | Read | BOOL | 02
407 | 2202-NK-SG-102-B.08OC_1 | 1612-PM-611B_PERMIT.MCU | MCU.1612-PM-611B - Desuperheater Water Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 406 | Read | BOOL | 02
408 | 2202-NK-SG-102-B.08OC_1 | 1612-PM-611B_FAULT.MCU | MCU.1612-PM-611B - Desuperheater Water Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 407 | Read | BOOL | 02
409 | 2202-NK-SG-102-B.08OC_1 | 1612-PM-611B_STA.MCU | MCU.1612-PM-611B - Desuperheater Water Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 408 | Read | BOOL | 02
410 | 2202-NK-SG-102-B.08OC_1 | 1612-PM-611B_EM_STOP.MCU | MCU.1612-PM-611B - Desuperheater Water Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 409 | Read | BOOL | 02
411 | 2202-NK-SG-102-B.08OC_1 | 1612-PM-611B_SWITCH_ON.MCU | MCU.1612-PM-611B - Desuperheater Water Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 410 | Read | BOOL | 02
412 | 2202-NK-SG-102-B.08OC_1 | 1612-PM-611B_MCCB POSITION.MCU | MCU.1612-PM-611B - Desuperheater Water Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 411 | Read | BOOL | 02
413 | 2202-NK-SG-102-B.08OC_1 | 1612-PM-611B_REDAY.MCU | MCU.1612-PM-611B - Desuperheater Water Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 412 | Read | BOOL | 02
414 | 2202-NK-SG-102-B.08OC_2 | 1612-PM-001B_TX.MCU | MCU.1612-PM-001B - oil pump motor_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 413 | Read | BOOL | 02
415 | 2202-NK-SG-102-B.08OC_2 | 1612-PM-001B_PERMIT.MCU | MCU.1612-PM-001B - oil pump motor_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 414 | Read | BOOL | 02
416 | 2202-NK-SG-102-B.08OC_2 | 1612-PM-001B_FAULT.MCU | MCU.1612-PM-001B - oil pump motor_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 415 | Read | BOOL | 02
417 | 2202-NK-SG-102-B.08OC_2 | 1612-PM-001B_STA.MCU | MCU.1612-PM-001B - oil pump motor_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 416 | Read | BOOL | 02
418 | 2202-NK-SG-102-B.08OC_2 | 1612-PM-001B_EM_STOP.MCU | MCU.1612-PM-001B - oil pump motor_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 417 | Read | BOOL | 02
419 | 2202-NK-SG-102-B.08OC_2 | 1612-PM-001B_SWITCH_ON.MCU | MCU.1612-PM-001B - oil pump motor_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 418 | Read | BOOL | 02
420 | 2202-NK-SG-102-B.08OC_2 | 1612-PM-001B_MCCB POSITION.MCU | MCU.1612-PM-001B - oil pump motor_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 419 | Read | BOOL | 02
421 | 2202-NK-SG-102-B.08OC_2 | 1612-PM-001B_REDAY.MCU | MCU.1612-PM-001B - oil pump motor_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 420 | Read | BOOL | 02
422 | 2202-NK-SG-102-B.08OC_3 | 1612-P-611B.HE-JB_TX.MCU | MCU.1612-P-611B.HE-JB - Oil heater junction box_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 421 | Read | BOOL | 02
423 | 2202-NK-SG-102-B.08OC_3 | 1612-P-611B.HE-JB_PERMIT.MCU | MCU.1612-P-611B.HE-JB - Oil heater junction box_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 422 | Read | BOOL | 02
424 | 2202-NK-SG-102-B.08OC_3 | 1612-P-611B.HE-JB_FAULT.MCU | MCU.1612-P-611B.HE-JB - Oil heater junction box_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 423 | Read | BOOL | 02
425 | 2202-NK-SG-102-B.08OC_3 | 1612-P-611B.HE-JB_STA.MCU | MCU.1612-P-611B.HE-JB - Oil heater junction box_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 424 | Read | BOOL | 02
426 | 2202-NK-SG-102-B.08OC_3 | 1612-P-611B.HE-JB_EM_STOP.MCU | MCU.1612-P-611B.HE-JB - Oil heater junction box_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 425 | Read | BOOL | 02
427 | 2202-NK-SG-102-B.08OC_3 | 1612-P-611B.HE-JB_SWITCH_ON.MCU | MCU.1612-P-611B.HE-JB - Oil heater junction box_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 426 | Read | BOOL | 02
428 | 2202-NK-SG-102-B.08OC_3 | 1612-P-611B.HE-JB_MCCB POSITION.MCU | MCU.1612-P-611B.HE-JB - Oil heater junction box_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 427 | Read | BOOL | 02
429 | 2202-NK-SG-102-B.08OC_3 | 1612-P-611B.HE-JB_REDAY.MCU | MCU.1612-P-611B.HE-JB - Oil heater junction box_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 428 | Read | BOOL | 02
430 | 2202-NK-SG-102-B.08OC_4 | 1110-KM-101B-2_TX.MCU | MCU.1110-KM-101B-2 - Barring motor_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 429 | Read | BOOL | 02
431 | 2202-NK-SG-102-B.08OC_4 | 1110-KM-101B-2_PERMIT.MCU | MCU.1110-KM-101B-2 - Barring motor_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 430 | Read | BOOL | 02
432 | 2202-NK-SG-102-B.08OC_4 | 1110-KM-101B-2_FAULT.MCU | MCU.1110-KM-101B-2 - Barring motor_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 431 | Read | BOOL | 02
433 | 2202-NK-SG-102-B.08OC_4 | 1110-KM-101B-2_STA.MCU | MCU.1110-KM-101B-2 - Barring motor_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 432 | Read | BOOL | 02
434 | 2202-NK-SG-102-B.08OC_4 | 1110-KM-101B-2_EM_STOP.MCU | MCU.1110-KM-101B-2 - Barring motor_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 433 | Read | BOOL | 02
435 | 2202-NK-SG-102-B.08OC_4 | 1110-KM-101B-2_SWITCH_ON.MCU | MCU.1110-KM-101B-2 - Barring motor_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 434 | Read | BOOL | 02
436 | 2202-NK-SG-102-B.08OC_4 | 1110-KM-101B-2_MCCB POSITION.MCU | MCU.1110-KM-101B-2 - Barring motor_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 435 | Read | BOOL | 02
437 | 2202-NK-SG-102-B.08OC_4 | 1110-KM-101B-2_REDAY.MCU | MCU.1110-KM-101B-2 - Barring motor_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 436 | Read | BOOL | 02
438 | 2202-NK-SG-102-B.08OC_5 | 1110-PM-132A_TX.MCU | MCU.1110-PM-132A - Oil pump motor 1_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 437 | Read | BOOL | 02
439 | 2202-NK-SG-102-B.08OC_5 | 1110-PM-132A_PERMIT.MCU | MCU.1110-PM-132A - Oil pump motor 1_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 438 | Read | BOOL | 02
440 | 2202-NK-SG-102-B.08OC_5 | 1110-PM-132A_FAULT.MCU | MCU.1110-PM-132A - Oil pump motor 1_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 439 | Read | BOOL | 02
441 | 2202-NK-SG-102-B.08OC_5 | 1110-PM-132A_STA.MCU | MCU.1110-PM-132A - Oil pump motor 1_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 440 | Read | BOOL | 02
442 | 2202-NK-SG-102-B.08OC_5 | 1110-PM-132A_EM_STOP.MCU | MCU.1110-PM-132A - Oil pump motor 1_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 441 | Read | BOOL | 02
443 | 2202-NK-SG-102-B.08OC_5 | 1110-PM-132A_SWITCH_ON.MCU | MCU.1110-PM-132A - Oil pump motor 1_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 442 | Read | BOOL | 02
444 | 2202-NK-SG-102-B.08OC_5 | 1110-PM-132A_MCCB POSITION.MCU | MCU.1110-PM-132A - Oil pump motor 1_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 443 | Read | BOOL | 02
445 | 2202-NK-SG-102-B.08OC_5 | 1110-PM-132A_REDAY.MCU | MCU.1110-PM-132A - Oil pump motor 1_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 444 | Read | BOOL | 02
446 | 2202-NK-SG-102-B.08OC_6 | 1110-PM-132B_TX.MCU | MCU.1110-PM-132B - Oil pump motor 2_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 445 | Read | BOOL | 02
447 | 2202-NK-SG-102-B.08OC_6 | 1110-PM-132B_PERMIT.MCU | MCU.1110-PM-132B - Oil pump motor 2_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 446 | Read | BOOL | 02
448 | 2202-NK-SG-102-B.08OC_6 | 1110-PM-132B_FAULT.MCU | MCU.1110-PM-132B - Oil pump motor 2_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 447 | Read | BOOL | 02
449 | 2202-NK-SG-102-B.08OC_6 | 1110-PM-132B_STA.MCU | MCU.1110-PM-132B - Oil pump motor 2_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 448 | Read | BOOL | 02
450 | 2202-NK-SG-102-B.08OC_6 | 1110-PM-132B_EM_STOP.MCU | MCU.1110-PM-132B - Oil pump motor 2_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 449 | Read | BOOL | 02
451 | 2202-NK-SG-102-B.08OC_6 | 1110-PM-132B_SWITCH_ON.MCU | MCU.1110-PM-132B - Oil pump motor 2_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 450 | Read | BOOL | 02
452 | 2202-NK-SG-102-B.08OC_6 | 1110-PM-132B_MCCB POSITION.MCU | MCU.1110-PM-132B - Oil pump motor 2_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 451 | Read | BOOL | 02
453 | 2202-NK-SG-102-B.08OC_6 | 1110-PM-132B_REDAY.MCU | MCU.1110-PM-132B - Oil pump motor 2_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 452 | Read | BOOL | 02
454 | 2202-NK-SG-102-B.08OC_7 | 1110-KM-101B.EH02_TX.MCU | MCU.1110-KM-101B.EH02 - Electric heater for crankcase_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 453 | Read | BOOL | 02
455 | 2202-NK-SG-102-B.08OC_7 | 1110-KM-101B.EH02_PERMIT.MCU | MCU.1110-KM-101B.EH02 - Electric heater for crankcase_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 454 | Read | BOOL | 02
456 | 2202-NK-SG-102-B.08OC_7 | 1110-KM-101B.EH02_FAULT.MCU | MCU.1110-KM-101B.EH02 - Electric heater for crankcase_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 455 | Read | BOOL | 02
457 | 2202-NK-SG-102-B.08OC_7 | 1110-KM-101B.EH02_STA.MCU | MCU.1110-KM-101B.EH02 - Electric heater for crankcase_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 456 | Read | BOOL | 02
458 | 2202-NK-SG-102-B.08OC_7 | 1110-KM-101B.EH02_EM_STOP.MCU | MCU.1110-KM-101B.EH02 - Electric heater for crankcase_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 457 | Read | BOOL | 02
459 | 2202-NK-SG-102-B.08OC_7 | 1110-KM-101B.EH02_SWITCH_ON.MCU | MCU.1110-KM-101B.EH02 - Electric heater for crankcase_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 458 | Read | BOOL | 02
460 | 2202-NK-SG-102-B.08OC_7 | 1110-KM-101B.EH02_MCCB POSITION.MCU | MCU.1110-KM-101B.EH02 - Electric heater for crankcase_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 459 | Read | BOOL | 02
461 | 2202-NK-SG-102-B.08OC_7 | 1110-KM-101B.EH02_REDAY.MCU | MCU.1110-KM-101B.EH02 - Electric heater for crankcase_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 460 | Read | BOOL | 02
462 | 2202-NK-SG-102-B.08OC_8 | 2202-NK-SG-102-B.08OC_8_TX.MCU | MCU.2202-NK-SG-102-B.08OC_8 - SPARE_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 461 | Read | BOOL | 02
463 | 2202-NK-SG-102-B.08OC_8 | 2202-NK-SG-102-B.08OC_8_PERMIT.MCU | MCU.2202-NK-SG-102-B.08OC_8 - SPARE_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 462 | Read | BOOL | 02
464 | 2202-NK-SG-102-B.08OC_8 | 2202-NK-SG-102-B.08OC_8_FAULT.MCU | MCU.2202-NK-SG-102-B.08OC_8 - SPARE_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 463 | Read | BOOL | 02
465 | 2202-NK-SG-102-B.08OC_8 | 2202-NK-SG-102-B.08OC_8_STA.MCU | MCU.2202-NK-SG-102-B.08OC_8 - SPARE_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 464 | Read | BOOL | 02
466 | 2202-NK-SG-102-B.08OC_8 | 2202-NK-SG-102-B.08OC_8_EM_STOP.MCU | MCU.2202-NK-SG-102-B.08OC_8 - SPARE_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 465 | Read | BOOL | 02
467 | 2202-NK-SG-102-B.08OC_8 | 2202-NK-SG-102-B.08OC_8_SWITCH_ON.MCU | MCU.2202-NK-SG-102-B.08OC_8 - SPARE_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 466 | Read | BOOL | 02
468 | 2202-NK-SG-102-B.08OC_8 | 2202-NK-SG-102-B.08OC_8_MCCB POSITION.MCU | MCU.2202-NK-SG-102-B.08OC_8 - SPARE_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 467 | Read | BOOL | 02
469 | 2202-NK-SG-102-B.08OC_8 | 2202-NK-SG-102-B.08OC_8_REDAY.MCU | MCU.2202-NK-SG-102-B.08OC_8 - SPARE_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 468 | Read | BOOL | 02
470 | 2202-NK-SG-102-B.10OC_1 | 1110-PM-133B_TX.MCU | MCU.1110-PM-133B - Water pump motor 2_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 469 | Read | BOOL | 02
471 | 2202-NK-SG-102-B.10OC_1 | 1110-PM-133B_PERMIT.MCU | MCU.1110-PM-133B - Water pump motor 2_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 470 | Read | BOOL | 02
472 | 2202-NK-SG-102-B.10OC_1 | 1110-PM-133B_FAULT.MCU | MCU.1110-PM-133B - Water pump motor 2_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 471 | Read | BOOL | 02
473 | 2202-NK-SG-102-B.10OC_1 | 1110-PM-133B_STA.MCU | MCU.1110-PM-133B - Water pump motor 2_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 472 | Read | BOOL | 02
474 | 2202-NK-SG-102-B.10OC_1 | 1110-PM-133B_EM_STOP.MCU | MCU.1110-PM-133B - Water pump motor 2_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 473 | Read | BOOL | 02
475 | 2202-NK-SG-102-B.10OC_1 | 1110-PM-133B_SWITCH_ON.MCU | MCU.1110-PM-133B - Water pump motor 2_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 474 | Read | BOOL | 02
476 | 2202-NK-SG-102-B.10OC_1 | 1110-PM-133B_MCCB POSITION.MCU | MCU.1110-PM-133B - Water pump motor 2_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 475 | Read | BOOL | 02
477 | 2202-NK-SG-102-B.10OC_1 | 1110-PM-133B_REDAY.MCU | MCU.1110-PM-133B - Water pump motor 2_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 476 | Read | BOOL | 02
478 | 2202-NK-SG-102-B.10OC_2 | 1130-KM-301B_TX.MCU | MCU.1130-KM-301B - Barring motor_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 477 | Read | BOOL | 02
479 | 2202-NK-SG-102-B.10OC_2 | 1130-KM-301B_PERMIT.MCU | MCU.1130-KM-301B - Barring motor_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 478 | Read | BOOL | 02
480 | 2202-NK-SG-102-B.10OC_2 | 1130-KM-301B_FAULT.MCU | MCU.1130-KM-301B - Barring motor_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 479 | Read | BOOL | 02
481 | 2202-NK-SG-102-B.10OC_2 | 1130-KM-301B_STA.MCU | MCU.1130-KM-301B - Barring motor_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 480 | Read | BOOL | 02
482 | 2202-NK-SG-102-B.10OC_2 | 1130-KM-301B_EM_STOP.MCU | MCU.1130-KM-301B - Barring motor_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 481 | Read | BOOL | 02
483 | 2202-NK-SG-102-B.10OC_2 | 1130-KM-301B_SWITCH_ON.MCU | MCU.1130-KM-301B - Barring motor_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 482 | Read | BOOL | 02
484 | 2202-NK-SG-102-B.10OC_2 | 1130-KM-301B_MCCB POSITION.MCU | MCU.1130-KM-301B - Barring motor_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 483 | Read | BOOL | 02
485 | 2202-NK-SG-102-B.10OC_2 | 1130-KM-301B_REDAY.MCU | MCU.1130-KM-301B - Barring motor_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 484 | Read | BOOL | 02
486 | 2202-NK-SG-102-B.10OC_3 | 1130-PM-332A_TX.MCU | MCU.1130-PM-332A - Main oil pump motor_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 485 | Read | BOOL | 02
487 | 2202-NK-SG-102-B.10OC_3 | 1130-PM-332A_PERMIT.MCU | MCU.1130-PM-332A - Main oil pump motor_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 486 | Read | BOOL | 02
488 | 2202-NK-SG-102-B.10OC_3 | 1130-PM-332A_FAULT.MCU | MCU.1130-PM-332A - Main oil pump motor_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 487 | Read | BOOL | 02
489 | 2202-NK-SG-102-B.10OC_3 | 1130-PM-332A_STA.MCU | MCU.1130-PM-332A - Main oil pump motor_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 488 | Read | BOOL | 02
490 | 2202-NK-SG-102-B.10OC_3 | 1130-PM-332A_EM_STOP.MCU | MCU.1130-PM-332A - Main oil pump motor_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 489 | Read | BOOL | 02
491 | 2202-NK-SG-102-B.10OC_3 | 1130-PM-332A_SWITCH_ON.MCU | MCU.1130-PM-332A - Main oil pump motor_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 490 | Read | BOOL | 02
492 | 2202-NK-SG-102-B.10OC_3 | 1130-PM-332A_MCCB POSITION.MCU | MCU.1130-PM-332A - Main oil pump motor_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 491 | Read | BOOL | 02
493 | 2202-NK-SG-102-B.10OC_3 | 1130-PM-332A_REDAY.MCU | MCU.1130-PM-332A - Main oil pump motor_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 492 | Read | BOOL | 02
494 | 2202-NK-SG-102-B.10OC_4 | 1130-PM-332B_TX.MCU | MCU.1130-PM-332B - Auxiliary oil pump motor_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 493 | Read | BOOL | 02
495 | 2202-NK-SG-102-B.10OC_4 | 1130-PM-332B_PERMIT.MCU | MCU.1130-PM-332B - Auxiliary oil pump motor_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 494 | Read | BOOL | 02
496 | 2202-NK-SG-102-B.10OC_4 | 1130-PM-332B_FAULT.MCU | MCU.1130-PM-332B - Auxiliary oil pump motor_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 495 | Read | BOOL | 02
497 | 2202-NK-SG-102-B.10OC_4 | 1130-PM-332B_STA.MCU | MCU.1130-PM-332B - Auxiliary oil pump motor_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 496 | Read | BOOL | 02
498 | 2202-NK-SG-102-B.10OC_4 | 1130-PM-332B_EM_STOP.MCU | MCU.1130-PM-332B - Auxiliary oil pump motor_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 497 | Read | BOOL | 02
499 | 2202-NK-SG-102-B.10OC_4 | 1130-PM-332B_SWITCH_ON.MCU | MCU.1130-PM-332B - Auxiliary oil pump motor_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 498 | Read | BOOL | 02
500 | 2202-NK-SG-102-B.10OC_4 | 1130-PM-332B_MCCB POSITION.MCU | MCU.1130-PM-332B - Auxiliary oil pump motor_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 499 | Read | BOOL | 02
501 | 2202-NK-SG-102-B.10OC_4 | 1130-PM-332B_REDAY.MCU | MCU.1130-PM-332B - Auxiliary oil pump motor_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 500 | Read | BOOL | 02
502 | 2202-NK-SG-102-B.10OC_5 | 1130-V-332B.EH_TX.MCU | MCU.1130-V-332B.EH - Lube oil tank heater_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 501 | Read | BOOL | 02
503 | 2202-NK-SG-102-B.10OC_5 | 1130-V-332B.EH_PERMIT.MCU | MCU.1130-V-332B.EH - Lube oil tank heater_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 502 | Read | BOOL | 02
504 | 2202-NK-SG-102-B.10OC_5 | 1130-V-332B.EH_FAULT.MCU | MCU.1130-V-332B.EH - Lube oil tank heater_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 503 | Read | BOOL | 02
505 | 2202-NK-SG-102-B.10OC_5 | 1130-V-332B.EH_STA.MCU | MCU.1130-V-332B.EH - Lube oil tank heater_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 504 | Read | BOOL | 02
506 | 2202-NK-SG-102-B.10OC_5 | 1130-V-332B.EH_EM_STOP.MCU | MCU.1130-V-332B.EH - Lube oil tank heater_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 505 | Read | BOOL | 02
507 | 2202-NK-SG-102-B.10OC_5 | 1130-V-332B.EH_SWITCH_ON.MCU | MCU.1130-V-332B.EH - Lube oil tank heater_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 506 | Read | BOOL | 02
508 | 2202-NK-SG-102-B.10OC_5 | 1130-V-332B.EH_MCCB POSITION.MCU | MCU.1130-V-332B.EH - Lube oil tank heater_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 507 | Read | BOOL | 02
509 | 2202-NK-SG-102-B.10OC_5 | 1130-V-332B.EH_REDAY.MCU | MCU.1130-V-332B.EH - Lube oil tank heater_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 508 | Read | BOOL | 02
510 | 2202-NK-SG-102-B.12OC_1 | 2701-PK-1501B-M_TX.MCU | MCU.2701-PK-1501B-M - "ITF Waste Gas FanAcoustic Enclosure Fan"_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 509 | Read | BOOL | 02
511 | 2202-NK-SG-102-B.12OC_1 | 2701-PK-1501B-M_PERMIT.MCU | MCU.2701-PK-1501B-M - "ITF Waste Gas FanAcoustic Enclosure Fan"_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 510 | Read | BOOL | 02
512 | 2202-NK-SG-102-B.12OC_1 | 2701-PK-1501B-M_FAULT.MCU | MCU.2701-PK-1501B-M - "ITF Waste Gas FanAcoustic Enclosure Fan"_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 511 | Read | BOOL | 02
513 | 2202-NK-SG-102-B.12OC_1 | 2701-PK-1501B-M_STA.MCU | MCU.2701-PK-1501B-M - "ITF Waste Gas FanAcoustic Enclosure Fan"_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 512 | Read | BOOL | 02
514 | 2202-NK-SG-102-B.12OC_1 | 2701-PK-1501B-M_EM_STOP.MCU | MCU.2701-PK-1501B-M - "ITF Waste Gas FanAcoustic Enclosure Fan"_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 513 | Read | BOOL | 02
515 | 2202-NK-SG-102-B.12OC_1 | 2701-PK-1501B-M_SWITCH_ON.MCU | MCU.2701-PK-1501B-M - "ITF Waste Gas FanAcoustic Enclosure Fan"_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 514 | Read | BOOL | 02
516 | 2202-NK-SG-102-B.12OC_1 | 2701-PK-1501B-M_MCCB POSITION.MCU | MCU.2701-PK-1501B-M - "ITF Waste Gas FanAcoustic Enclosure Fan"_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 515 | Read | BOOL | 02
517 | 2202-NK-SG-102-B.12OC_1 | 2701-PK-1501B-M_REDAY.MCU | MCU.2701-PK-1501B-M - "ITF Waste Gas FanAcoustic Enclosure Fan"_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 516 | Read | BOOL | 02
518 | 2202-NK-SG-102-B.12OC_2 | 2701-PM-1216_TX.MCU | MCU.2701-PM-1216 - Slop Drum Water Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 517 | Read | BOOL | 02
519 | 2202-NK-SG-102-B.12OC_2 | 2701-PM-1216_PERMIT.MCU | MCU.2701-PM-1216 - Slop Drum Water Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 518 | Read | BOOL | 02
520 | 2202-NK-SG-102-B.12OC_2 | 2701-PM-1216_FAULT.MCU | MCU.2701-PM-1216 - Slop Drum Water Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 519 | Read | BOOL | 02
521 | 2202-NK-SG-102-B.12OC_2 | 2701-PM-1216_STA.MCU | MCU.2701-PM-1216 - Slop Drum Water Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 520 | Read | BOOL | 02
522 | 2202-NK-SG-102-B.12OC_2 | 2701-PM-1216_EM_STOP.MCU | MCU.2701-PM-1216 - Slop Drum Water Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 521 | Read | BOOL | 02
523 | 2202-NK-SG-102-B.12OC_2 | 2701-PM-1216_SWITCH_ON.MCU | MCU.2701-PM-1216 - Slop Drum Water Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 522 | Read | BOOL | 02
524 | 2202-NK-SG-102-B.12OC_2 | 2701-PM-1216_MCCB POSITION.MCU | MCU.2701-PM-1216 - Slop Drum Water Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 523 | Read | BOOL | 02
525 | 2202-NK-SG-102-B.12OC_2 | 2701-PM-1216_REDAY.MCU | MCU.2701-PM-1216 - Slop Drum Water Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 524 | Read | BOOL | 02
526 | 2202-NK-SG-102-B.12OC_3 | 2202-NK-SG-102-B.12OC_3_TX.MCU | MCU.2202-NK-SG-102-B.12OC_3 - SPARE_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 525 | Read | BOOL | 02
527 | 2202-NK-SG-102-B.12OC_3 | 2202-NK-SG-102-B.12OC_3_PERMIT.MCU | MCU.2202-NK-SG-102-B.12OC_3 - SPARE_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 526 | Read | BOOL | 02
528 | 2202-NK-SG-102-B.12OC_3 | 2202-NK-SG-102-B.12OC_3_FAULT.MCU | MCU.2202-NK-SG-102-B.12OC_3 - SPARE_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 527 | Read | BOOL | 02
529 | 2202-NK-SG-102-B.12OC_3 | 2202-NK-SG-102-B.12OC_3_STA.MCU | MCU.2202-NK-SG-102-B.12OC_3 - SPARE_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 528 | Read | BOOL | 02
530 | 2202-NK-SG-102-B.12OC_3 | 2202-NK-SG-102-B.12OC_3_EM_STOP.MCU | MCU.2202-NK-SG-102-B.12OC_3 - SPARE_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 529 | Read | BOOL | 02
531 | 2202-NK-SG-102-B.12OC_3 | 2202-NK-SG-102-B.12OC_3_SWITCH_ON.MCU | MCU.2202-NK-SG-102-B.12OC_3 - SPARE_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 530 | Read | BOOL | 02
532 | 2202-NK-SG-102-B.12OC_3 | 2202-NK-SG-102-B.12OC_3_MCCB POSITION.MCU | MCU.2202-NK-SG-102-B.12OC_3 - SPARE_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 531 | Read | BOOL | 02
533 | 2202-NK-SG-102-B.12OC_3 | 2202-NK-SG-102-B.12OC_3_REDAY.MCU | MCU.2202-NK-SG-102-B.12OC_3 - SPARE_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 532 | Read | BOOL | 02
534 | 2202-NK-SG-102-B.12OC_4 | 2701-PM-1701B_TX.MCU | MCU.2701-PM-1701B - TBC Solution Dosing pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 533 | Read | BOOL | 02
535 | 2202-NK-SG-102-B.12OC_4 | 2701-PM-1701B_PERMIT.MCU | MCU.2701-PM-1701B - TBC Solution Dosing pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 534 | Read | BOOL | 02
536 | 2202-NK-SG-102-B.12OC_4 | 2701-PM-1701B_FAULT.MCU | MCU.2701-PM-1701B - TBC Solution Dosing pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 535 | Read | BOOL | 02
537 | 2202-NK-SG-102-B.12OC_4 | 2701-PM-1701B_STA.MCU | MCU.2701-PM-1701B - TBC Solution Dosing pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 536 | Read | BOOL | 02
538 | 2202-NK-SG-102-B.12OC_4 | 2701-PM-1701B_EM_STOP.MCU | MCU.2701-PM-1701B - TBC Solution Dosing pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 537 | Read | BOOL | 02
539 | 2202-NK-SG-102-B.12OC_4 | 2701-PM-1701B_SWITCH_ON.MCU | MCU.2701-PM-1701B - TBC Solution Dosing pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 538 | Read | BOOL | 02
540 | 2202-NK-SG-102-B.12OC_4 | 2701-PM-1701B_MCCB POSITION.MCU | MCU.2701-PM-1701B - TBC Solution Dosing pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 539 | Read | BOOL | 02
541 | 2202-NK-SG-102-B.12OC_4 | 2701-PM-1701B_REDAY.MCU | MCU.2701-PM-1701B - TBC Solution Dosing pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 540 | Read | BOOL | 02
542 | 2202-NK-SG-102-B.12OC_5 | 2701-PM-1206B_TX.MCU | MCU.2701-PM-1206B - Benzene-Toluene FractionTransfer Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 541 | Read | BOOL | 02
543 | 2202-NK-SG-102-B.12OC_5 | 2701-PM-1206B_PERMIT.MCU | MCU.2701-PM-1206B - Benzene-Toluene FractionTransfer Pump_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 542 | Read | BOOL | 02
544 | 2202-NK-SG-102-B.12OC_5 | 2701-PM-1206B_FAULT.MCU | MCU.2701-PM-1206B - Benzene-Toluene FractionTransfer Pump_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 543 | Read | BOOL | 02
545 | 2202-NK-SG-102-B.12OC_5 | 2701-PM-1206B_STA.MCU | MCU.2701-PM-1206B - Benzene-Toluene FractionTransfer Pump_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 544 | Read | BOOL | 02
546 | 2202-NK-SG-102-B.12OC_5 | 2701-PM-1206B_EM_STOP.MCU | MCU.2701-PM-1206B - Benzene-Toluene FractionTransfer Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 545 | Read | BOOL | 02
547 | 2202-NK-SG-102-B.12OC_5 | 2701-PM-1206B_SWITCH_ON.MCU | MCU.2701-PM-1206B - Benzene-Toluene FractionTransfer Pump_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 546 | Read | BOOL | 02
548 | 2202-NK-SG-102-B.12OC_5 | 2701-PM-1206B_MCCB POSITION.MCU | MCU.2701-PM-1206B - Benzene-Toluene FractionTransfer Pump_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 547 | Read | BOOL | 02
549 | 2202-NK-SG-102-B.12OC_5 | 2701-PM-1206B_REDAY.MCU | MCU.2701-PM-1206B - Benzene-Toluene FractionTransfer Pump_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 548 | Read | BOOL | 02
550 | 2202-NK-SG-102-B.12OC_6 | 2202-NK-SG-102-B.12OC_6_TX.MCU | MCU.2202-NK-SG-102-B.12OC_6 - SPARE_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 549 | Read | BOOL | 02
551 | 2202-NK-SG-102-B.12OC_6 | 2202-NK-SG-102-B.12OC_6_PERMIT.MCU | MCU.2202-NK-SG-102-B.12OC_6 - SPARE_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 550 | Read | BOOL | 02
552 | 2202-NK-SG-102-B.12OC_6 | 2202-NK-SG-102-B.12OC_6_FAULT.MCU | MCU.2202-NK-SG-102-B.12OC_6 - SPARE_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 551 | Read | BOOL | 02
553 | 2202-NK-SG-102-B.12OC_6 | 2202-NK-SG-102-B.12OC_6_STA.MCU | MCU.2202-NK-SG-102-B.12OC_6 - SPARE_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 552 | Read | BOOL | 02
554 | 2202-NK-SG-102-B.12OC_6 | 2202-NK-SG-102-B.12OC_6_EM_STOP.MCU | MCU.2202-NK-SG-102-B.12OC_6 - SPARE_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 553 | Read | BOOL | 02
555 | 2202-NK-SG-102-B.12OC_6 | 2202-NK-SG-102-B.12OC_6_SWITCH_ON.MCU | MCU.2202-NK-SG-102-B.12OC_6 - SPARE_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 554 | Read | BOOL | 02
556 | 2202-NK-SG-102-B.12OC_6 | 2202-NK-SG-102-B.12OC_6_MCCB POSITION.MCU | MCU.2202-NK-SG-102-B.12OC_6 - SPARE_MCCB Working Position 1:Working Position 0:Test Position |  | MCCB Working Position 1:Working Position 0:Test Position |  |  |  |  | 1 | Permanent | 1 | 555 | Read | BOOL | 02
557 | 2202-NK-SG-102-B.12OC_6 | 2202-NK-SG-102-B.12OC_6_REDAY.MCU | MCU.2202-NK-SG-102-B.12OC_6 - SPARE_Motor Ready 1:Ready 0:Not Ready |  | Motor Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 556 | Read | BOOL | 02
558 | 2202-NK-SG-102-B.16OC_1 | 1130-PM-301B_TX.MCU | MCU.1130-PM-301B - DM Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 557 | Read | BOOL | 02
559 | 2202-NK-SG-102-B.16OC_1 | 1130-PM-301B_EM_STOP.MCU | MCU.1130-PM-301B - DM Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 558 | Read | BOOL | 02
560 | 2202-NK-SG-102-B.16OC_2 | 1130-PM-303B_TX.MCU | MCU.1130-PM-303B - Condensate Stripper Bottom Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 559 | Read | BOOL | 02
561 | 2202-NK-SG-102-B.16OC_2 | 1130-PM-303B_EM_STOP.MCU | MCU.1130-PM-303B - Condensate Stripper Bottom Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 560 | Read | BOOL | 02
562 | 2202-NK-SG-102-B.16OC_3 | 1612-PM-606B_TX.MCU | MCU.1612-PM-606B - LLP Condensate Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 561 | Read | BOOL | 02
563 | 2202-NK-SG-102-B.16OC_3 | 1612-PM-606B_EM_STOP.MCU | MCU.1612-PM-606B - LLP Condensate Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 562 | Read | BOOL | 02
564 | 2202-NK-SG-102-B.18OC_1 | 2701-PM-1202B_TX.MCU | MCU.2701-PM-1202B - Ethylbenzene transfer pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 563 | Read | BOOL | 02
565 | 2202-NK-SG-102-B.18OC_1 | 2701-PM-1202B_EM_STOP.MCU | MCU.2701-PM-1202B - Ethylbenzene transfer pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 564 | Read | BOOL | 02
566 | 2202-NK-SG-102-B.18OC_2 | 2701-PM-1201B_TX.MCU | MCU.2701-PM-1201B - Benzene transfer pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 565 | Read | BOOL | 02
567 | 2202-NK-SG-102-B.18OC_2 | 2701-PM-1201B_EM_STOP.MCU | MCU.2701-PM-1201B - Benzene transfer pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 566 | Read | BOOL | 02
568 | 2202-NK-SG-102-B.18OC_3 | 2701-PM-1205S_TX.MCU | MCU.2701-PM-1205S - SM Transfer Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 567 | Read | BOOL | 02
569 | 2202-NK-SG-102-B.18OC_3 | 2701-PM-1205S_EM_STOP.MCU | MCU.2701-PM-1205S - SM Transfer Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 568 | Read | BOOL | 02
570 | 2202-NK-SG-102-B.20OC_2 | 2701-PM-1204B_TX.MCU | MCU.2701-PM-1204B - DM Transfer Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 569 | Read | BOOL | 02
571 | 2202-NK-SG-102-B.20OC_2 | 2701-PM-1204B_EM_STOP.MCU | MCU.2701-PM-1204B - DM Transfer Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 570 | Read | BOOL | 02
572 | 2202-NK-SG-102-B.20OC_1 | 2701-PM-1207B_TX.MCU | MCU.2701-PM-1207B - Heavy Tar Loading Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 571 | Read | BOOL | 02
573 | 2202-NK-SG-102-B.20OC_1 | 2701-PM-1207B_EM_STOP.MCU | MCU.2701-PM-1207B - Heavy Tar Loading Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 572 | Read | BOOL | 02
574 | 2202-NK-SG-102-B.20OC_3 | 2701-PM-1205A_TX.MCU | MCU.2701-PM-1205A - SM Transfer Pump_Communication Status 1:Communication Normal 0:Communication Interrupted |  | Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 573 | Read | BOOL | 02
575 | 2202-NK-SG-102-B.20OC_3 | 2701-PM-1205A_EM_STOP.MCU | MCU.2701-PM-1205A - SM Transfer Pump_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 574 | Read | BOOL | 02
576 | 2202-NK-SG-102-B.SS01_1 | 2202-NK-SG-102-B.SS01_1_PLC_TX.PLC | PLC.2202-NK-SG-102-B.SS01_1 - inlet switch+SOFT STARTER_SSR PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  | SSR PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 575 | Read | BOOL | 02
577 | 2202-NK-SG-102-B.SS01_1 | 1130-PM-301B_M1_PERMIT.PLC | PLC.1130-PM-301B - DM Pump_Circuit 1_Permitted State 1:Permit 0:Not Permit |  | Circuit 1_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 576 | Read | BOOL | 02
578 | 2202-NK-SG-102-B.SS01_1 | 1130-PM-301B_Q1_READY.PLC | PLC.1130-PM-301B - DM Pump_Circuit 1_Q1_Ready 1:Ready 0:Not Ready |  | Circuit 1_Q1_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 577 | Read | BOOL | 02
579 | 2202-NK-SG-102-B.SS01_1 | 1130-PM-301B_Q1_BYPS.PLC | PLC.1130-PM-301B - DM Pump_Circuit 1_Q1_Motor 1 Operation 1:Running 0:Stopped |  | Circuit 1_Q1_Motor 1 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 578 | Read | BOOL | 02
580 | 2202-NK-SG-102-B.SS01_1 | 1130-PM-301B_Q1_F.PLC | PLC.1130-PM-301B - DM Pump_Circuit 1_Q1_Motor 1 Fault 1:Fault 0:Normal |  | Circuit 1_Q1_Motor 1 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 579 | Read | BOOL | 02
581 | 2202-NK-SG-102-B.SS01_1 | 1130-PM-301B_QF1_ATUO.PLC | PLC.1130-PM-301B - DM Pump_Circuit 1_Q1_Remote_Local 1:Remote 0:Local |  | Circuit 1_Q1_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 580 | Read | BOOL | 02
582 | 2202-NK-SG-102-B.SS01_1 | 1130-PM-301B_QF1_STA.PLC | PLC.1130-PM-301B - DM Pump_Circuit 1_QF1_Switch Closing 1:Closed 0:Open |  | Circuit 1_QF1_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 581 | Read | BOOL | 02
583 | 2202-NK-SG-102-B.SS01_1 | 1130-PM-303B_M2_PERMIT.PLC | PLC.1130-PM-303B - Condensate Stripper Bottom Pump_Circuit 2_Permitted State 1:Permit 0:Not Permit |  | Circuit 2_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 582 | Read | BOOL | 02
584 | 2202-NK-SG-102-B.SS01_1 | 1130-PM-303B_Q2_READY.PLC | PLC.1130-PM-303B - Condensate Stripper Bottom Pump_Circuit 2_Q2_Ready 1:Ready 0:Not Ready |  | Circuit 2_Q2_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 583 | Read | BOOL | 02
585 | 2202-NK-SG-102-B.SS01_1 | 1130-PM-303B_Q2_BYPS.PLC | PLC.1130-PM-303B - Condensate Stripper Bottom Pump_Circuit 2_Q2_Motor 2 Operation 1:Running 0:Stopped |  | Circuit 2_Q2_Motor 2 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 584 | Read | BOOL | 02
586 | 2202-NK-SG-102-B.SS01_1 | 1130-PM-303B_Q2_F.PLC | PLC.1130-PM-303B - Condensate Stripper Bottom Pump_Circuit 2_Q2_Motor 2 Fault 1:Fault 0:Normal |  | Circuit 2_Q2_Motor 2 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 585 | Read | BOOL | 02
587 | 2202-NK-SG-102-B.SS01_1 | 1130-PM-303B_QF2_ATUO.PLC | PLC.1130-PM-303B - Condensate Stripper Bottom Pump_Circuit 2_Q2_Remote_Local 1:Remote 0:Local |  | Circuit 2_Q2_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 586 | Read | BOOL | 02
588 | 2202-NK-SG-102-B.SS01_1 | 1130-PM-303B_QF2_STA.PLC | PLC.1130-PM-303B - Condensate Stripper Bottom Pump_Circuit 2_QF2_Switch Closing 1:Closed 0:Open |  | Circuit 2_QF2_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 587 | Read | BOOL | 02
589 | 2202-NK-SG-102-B.SS01_1 | 1612-PM-606B_M3_PERMIT.PLC | PLC.1612-PM-606B - LLP Condensate Pump_Circuit 3_Permitted State 1:Permit 0:Not Permit |  | Circuit 3_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 588 | Read | BOOL | 02
590 | 2202-NK-SG-102-B.SS01_1 | 1612-PM-606B_Q3_READY.PLC | PLC.1612-PM-606B - LLP Condensate Pump_Circuit 3_Q3_Ready 1:Ready 0:Not Ready |  | Circuit 3_Q3_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 589 | Read | BOOL | 02
591 | 2202-NK-SG-102-B.SS01_1 | 1612-PM-606B_Q3_BYPS.PLC | PLC.1612-PM-606B - LLP Condensate Pump_Circuit 3_Q3_Motor 3 Operation 1:Running 0:Stopped |  | Circuit 3_Q3_Motor 3 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 590 | Read | BOOL | 02
592 | 2202-NK-SG-102-B.SS01_1 | 1612-PM-606B_Q3_F.PLC | PLC.1612-PM-606B - LLP Condensate Pump_Circuit 3_Q3_Motor 3 Fault 1:Fault 0:Normal |  | Circuit 3_Q3_Motor 3 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 591 | Read | BOOL | 02
593 | 2202-NK-SG-102-B.SS01_1 | 1612-PM-606B_QF3_ATUO.PLC | PLC.1612-PM-606B - LLP Condensate Pump_Circuit 3_Q3_Remote_Local 1:Remote 0:Local |  | Circuit 3_Q3_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 592 | Read | BOOL | 02
594 | 2202-NK-SG-102-B.SS01_1 | 1612-PM-606B_QF3_STA.PLC | PLC.1612-PM-606B - LLP Condensate Pump_Circuit 3_QF3_Switch Closing 1:Closed 0:Open |  | Circuit 3_QF3_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 593 | Read | BOOL | 02
595 | 2202-NK-SG-102-B.SS03_1 | 2202-NK-SG-102-B.SS03_1_PLC_TX.PLC | PLC.2202-NK-SG-102-B.SS03_1 - inlet switch+SOFT STARTER_SSR PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  | SSR PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 594 | Read | BOOL | 02
596 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1202B_M1_PERMIT.PLC | PLC.2701-PM-1202B - Ethylbenzene transfer pump_Circuit 1_Permitted State 1:Permit 0:Not Permit |  | Circuit 1_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 595 | Read | BOOL | 02
597 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1202B_Q1_READY.PLC | PLC.2701-PM-1202B - Ethylbenzene transfer pump_Circuit 1_Q1_Ready 1:Ready 0:Not Ready |  | Circuit 1_Q1_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 596 | Read | BOOL | 02
598 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1202B_Q1_BYPS.PLC | PLC.2701-PM-1202B - Ethylbenzene transfer pump_Circuit 1_Q1_Motor 1 Operation 1:Running 0:Stopped |  | Circuit 1_Q1_Motor 1 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 597 | Read | BOOL | 02
599 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1202B_Q1_F.PLC | PLC.2701-PM-1202B - Ethylbenzene transfer pump_Circuit 1_Q1_Motor 1 Fault 1:Fault 0:Normal |  | Circuit 1_Q1_Motor 1 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 598 | Read | BOOL | 02
600 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1202B_QF1_ATUO.PLC | PLC.2701-PM-1202B - Ethylbenzene transfer pump_Circuit 1_Q1_Remote_Local 1:Remote 0:Local |  | Circuit 1_Q1_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 599 | Read | BOOL | 02
601 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1202B_QF1_STA.PLC | PLC.2701-PM-1202B - Ethylbenzene transfer pump_Circuit 1_QF1_Switch Closing 1:Closed 0:Open |  | Circuit 1_QF1_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 600 | Read | BOOL | 02
602 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1201B_M2_PERMIT.PLC | PLC.2701-PM-1201B - Benzene transfer pump_Circuit 2_Permitted State 1:Permit 0:Not Permit |  | Circuit 2_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 601 | Read | BOOL | 02
603 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1201B_Q2_READY.PLC | PLC.2701-PM-1201B - Benzene transfer pump_Circuit 2_Q2_Ready 1:Ready 0:Not Ready |  | Circuit 2_Q2_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 602 | Read | BOOL | 02
604 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1201B_Q2_BYPS.PLC | PLC.2701-PM-1201B - Benzene transfer pump_Circuit 2_Q2_Motor 2 Operation 1:Running 0:Stopped |  | Circuit 2_Q2_Motor 2 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 603 | Read | BOOL | 02
605 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1201B_Q2_F.PLC | PLC.2701-PM-1201B - Benzene transfer pump_Circuit 2_Q2_Motor 2 Fault 1:Fault 0:Normal |  | Circuit 2_Q2_Motor 2 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 604 | Read | BOOL | 02
606 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1201B_QF2_ATUO.PLC | PLC.2701-PM-1201B - Benzene transfer pump_Circuit 2_Q2_Remote_Local 1:Remote 0:Local |  | Circuit 2_Q2_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 605 | Read | BOOL | 02
607 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1201B_QF2_STA.PLC | PLC.2701-PM-1201B - Benzene transfer pump_Circuit 2_QF2_Switch Closing 1:Closed 0:Open |  | Circuit 2_QF2_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 606 | Read | BOOL | 02
608 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1204B_M3_PERMIT.PLC | PLC.2701-PM-1204B - DM Transfer Pump_Circuit 3_Permitted State 1:Permit 0:Not Permit |  | Circuit 3_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 607 | Read | BOOL | 02
609 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1204B_Q3_READY.PLC | PLC.2701-PM-1204B - DM Transfer Pump_Circuit 3_Q3_Ready 1:Ready 0:Not Ready |  | Circuit 3_Q3_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 608 | Read | BOOL | 02
610 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1204B_Q3_BYPS.PLC | PLC.2701-PM-1204B - DM Transfer Pump_Circuit 3_Q3_Motor 3 Operation 1:Running 0:Stopped |  | Circuit 3_Q3_Motor 3 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 609 | Read | BOOL | 02
611 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1204B_Q3_F.PLC | PLC.2701-PM-1204B - DM Transfer Pump_Circuit 3_Q3_Motor 3 Fault 1:Fault 0:Normal |  | Circuit 3_Q3_Motor 3 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 610 | Read | BOOL | 02
612 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1204B_QF3_ATUO.PLC | PLC.2701-PM-1204B - DM Transfer Pump_Circuit 3_Q3_Remote_Local 1:Remote 0:Local |  | Circuit 3_Q3_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 611 | Read | BOOL | 02
613 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1204B_QF3_STA.PLC | PLC.2701-PM-1204B - DM Transfer Pump_Circuit 3_QF3_Switch Closing 1:Closed 0:Open |  | Circuit 3_QF3_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 612 | Read | BOOL | 02
614 | 2202-NK-SG-102-B.SS05_1 | 2202-NK-SG-102-B.SS05_1_PLC_TX.PLC | PLC.2202-NK-SG-102-B.SS05_1 - inlet switch+SOFT STARTER_SSR PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  | SSR PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 613 | Read | BOOL | 02
615 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1207B_M1_PERMIT.PLC | PLC.2701-PM-1207B - Heavy Tar Loading Pump_Circuit 1_Permitted State 1:Permit 0:Not Permit |  | Circuit 1_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 614 | Read | BOOL | 02
616 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1207B_Q1_READY.PLC | PLC.2701-PM-1207B - Heavy Tar Loading Pump_Circuit 1_Q1_Ready 1:Ready 0:Not Ready |  | Circuit 1_Q1_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 615 | Read | BOOL | 02
617 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1207B_Q1_BYPS.PLC | PLC.2701-PM-1207B - Heavy Tar Loading Pump_Circuit 1_Q1_Motor 1 Operation 1:Running 0:Stopped |  | Circuit 1_Q1_Motor 1 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 616 | Read | BOOL | 02
618 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1207B_Q1_F.PLC | PLC.2701-PM-1207B - Heavy Tar Loading Pump_Circuit 1_Q1_Motor 1 Fault 1:Fault 0:Normal |  | Circuit 1_Q1_Motor 1 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 617 | Read | BOOL | 02
619 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1207B_QF1_ATUO.PLC | PLC.2701-PM-1207B - Heavy Tar Loading Pump_Circuit 1_Q1_Remote_Local 1:Remote 0:Local |  | Circuit 1_Q1_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 618 | Read | BOOL | 02
620 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1207B_QF1_STA.PLC | PLC.2701-PM-1207B - Heavy Tar Loading Pump_Circuit 1_QF1_Switch Closing 1:Closed 0:Open |  | Circuit 1_QF1_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 619 | Read | BOOL | 02
621 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1205A_M2_PERMIT.PLC | PLC.2701-PM-1205A - SM Transfer Pump_Circuit 2_Permitted State 1:Permit 0:Not Permit |  | Circuit 2_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 620 | Read | BOOL | 02
622 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1205A_Q2_READY.PLC | PLC.2701-PM-1205A - SM Transfer Pump_Circuit 2_Q2_Ready 1:Ready 0:Not Ready |  | Circuit 2_Q2_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 621 | Read | BOOL | 02
623 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1205A_Q2_BYPS.PLC | PLC.2701-PM-1205A - SM Transfer Pump_Circuit 2_Q2_Motor 2 Operation 1:Running 0:Stopped |  | Circuit 2_Q2_Motor 2 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 622 | Read | BOOL | 02
624 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1205A_Q2_F.PLC | PLC.2701-PM-1205A - SM Transfer Pump_Circuit 2_Q2_Motor 2 Fault 1:Fault 0:Normal |  | Circuit 2_Q2_Motor 2 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 623 | Read | BOOL | 02
625 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1205A_QF2_ATUO.PLC | PLC.2701-PM-1205A - SM Transfer Pump_Circuit 2_Q2_Remote_Local 1:Remote 0:Local |  | Circuit 2_Q2_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 624 | Read | BOOL | 02
626 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1205A_QF2_STA.PLC | PLC.2701-PM-1205A - SM Transfer Pump_Circuit 2_QF2_Switch Closing 1:Closed 0:Open |  | Circuit 2_QF2_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 625 | Read | BOOL | 02
627 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1205S_M3_PERMIT.PLC | PLC.2701-PM-1205S - SM Transfer Pump_Circuit 3_Permitted State 1:Permit 0:Not Permit |  | Circuit 3_Permitted State 1:Permit 0:Not Permit |  |  |  |  | 1 | Permanent | 1 | 626 | Read | BOOL | 02
628 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1205S_Q3_READY.PLC | PLC.2701-PM-1205S - SM Transfer Pump_Circuit 3_Q3_Ready 1:Ready 0:Not Ready |  | Circuit 3_Q3_Ready 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 627 | Read | BOOL | 02
629 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1205S_Q3_BYPS.PLC | PLC.2701-PM-1205S - SM Transfer Pump_Circuit 3_Q3_Motor 3 Operation 1:Running 0:Stopped |  | Circuit 3_Q3_Motor 3 Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 628 | Read | BOOL | 02
630 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1205S_Q3_F.PLC | PLC.2701-PM-1205S - SM Transfer Pump_Circuit 3_Q3_Motor 3 Fault 1:Fault 0:Normal |  | Circuit 3_Q3_Motor 3 Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 629 | Read | BOOL | 02
631 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1205S_QF3_ATUO.PLC | PLC.2701-PM-1205S - SM Transfer Pump_Circuit 3_Q3_Remote_Local 1:Remote 0:Local |  | Circuit 3_Q3_Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 630 | Read | BOOL | 02
632 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1205S_QF3_STA.PLC | PLC.2701-PM-1205S - SM Transfer Pump_Circuit 3_QF3_Switch Closing 1:Closed 0:Open |  | Circuit 3_QF3_Switch Closing 1:Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 631 | Read | BOOL | 02
633 | 2202-NK-SG-102-B.22OC_1 | 2701-PK-1201B-M_TX.VFD | VFD.2701-PK-1201B-M - ITF Waste Gas Fan_VFD Communication Status 1:Communication Normal 0:Communication Interrupted |  | VFD Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 632 | Read | BOOL | 02
634 | 2202-NK-SG-102-B.22OC_1 | 2701-PK-1201B-M_TX.PLC | PLC.2701-PK-1201B-M - ITF Waste Gas Fan_VFD PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  | VFD PLC Communication Status 1:Communication Normal 0:Communication Interrupted |  |  |  |  | 1 | Permanent | 1 | 633 | Read | BOOL | 02
635 | 2202-NK-SG-102-B.22OC_1 | 2701-PK-1201B-M_PERMIT.PLC | PLC.2701-PK-1201B-M - ITF Waste Gas Fan_Permitted State 1:Permit 0:No Permit |  | Permitted State 1:Permit 0:No Permit |  |  |  |  | 1 | Permanent | 1 | 634 | Read | BOOL | 02
636 | 2202-NK-SG-102-B.22OC_1 | 2701-PK-1201B-M_LOC_REM.PLC | PLC.2701-PK-1201B-M - ITF Waste Gas Fan_Remote_Local 1:Remote 0:Local |  | Remote_Local 1:Remote 0:Local |  |  |  |  | 1 | Permanent | 1 | 635 | Read | BOOL | 02
637 | 2202-NK-SG-102-B.22OC_1 | 2701-PK-1201B-M_STA.PLC | PLC.2701-PK-1201B-M - ITF Waste Gas Fan_Motor Operation 1:Running 0:Stopped |  | Motor Operation 1:Running 0:Stopped |  |  |  |  | 1 | Permanent | 1 | 636 | Read | BOOL | 02
638 | 2202-NK-SG-102-B.22OC_1 | 2701-PK-1201B-M_REDAY.PLC | PLC.2701-PK-1201B-M - ITF Waste Gas Fan_Motor ALLReady 1:Ready 0:Not Ready |  | Motor ALLReady 1:Ready 0:Not Ready |  |  |  |  | 1 | Permanent | 1 | 637 | Read | BOOL | 02
639 | 2202-NK-SG-102-B.22OC_1 | 2701-PK-1201B-M_SWITCH_ON.PLC | PLC.2701-PK-1201B-M - ITF Waste Gas Fan_MCCB Closed 1:Closed Position 0:Open Position |  | MCCB Closed 1:Closed Position 0:Open Position |  |  |  |  | 1 | Permanent | 1 | 638 | Read | BOOL | 02
640 | 2202-NK-SG-102-B.22OC_1 | 2701-PK-1201B-M_DOORSTA.PLC | PLC.2701-PK-1201B-M - ITF Waste Gas Fan_Cabinet Door Closed 1:Cabinet Door Closed 0:Open |  | Cabinet Door Closed 1:Cabinet Door Closed 0:Open |  |  |  |  | 1 | Permanent | 1 | 639 | Read | BOOL | 02
641 | 2202-NK-SG-102-B.22OC_1 | 2701-PK-1201B-M_FAULT.PLC | PLC.2701-PK-1201B-M - ITF Waste Gas Fan_General Fault 1:Fault 0:Normal |  | General Fault 1:Fault 0:Normal |  |  |  |  | 1 | Permanent | 1 | 640 | Read | BOOL | 02
642 | 2202-NK-SG-102-B.22OC_1 | 2701-PK-1201B-M_EM_STOP.PLC | PLC.2701-PK-1201B-M - ITF Waste Gas Fan_Emergency shutdown 1:Emergency shutdown 0:Normal |  | Emergency shutdown 1:Emergency shutdown 0:Normal |  |  |  |  | 1 | Permanent | 1 | 641 | Read | BOOL | 02

## Register Table Function 03
№ п/п | Функциональное обозначение по проекту Project Functional Designation | Tег ПЛК / Hаименование переменной PLC Tag/Variable Name | Описание переменной Description of the variable | Единицы измерения Units of measurement | Шкала scale | LL | LA | HA | HH | Коэффициенты масштабирования Scaling factors | Тип сигнала (Импульс/Постоянный ) Signal type (Impulse/Permanent) | Тип регистра Register type | Адрес/бит Address/Bit | Тип доступа Access type | Тип данных Data type | Код функции Function code | Канал РСУ DCS channel | Tег РСУ / Hаименование переменной DCS Tag/Name variable | Функции РСУ DCS functions | Примечание note
1 | 2202-NK-SG-102-A.03OC_1 | 1115-PM-101A_I_A | 1115-PM-101A - R-101 Recycle Pumps_Phase A current | A | 0..88 |  |  |  |  | 1 | Permanent | 4 | 0 | Read | 32-Bit Floating | 03
2 | 2202-NK-SG-102-A.03OC_2 | 1630-PM-214A_I_A | 1630-PM-214A - R-101 Recycle Pumps_Phase A current | A | 0..44 |  |  |  |  | 1 | Permanent | 4 | 2 | Read | 32-Bit Floating | 03
3 | 2202-NK-SG-102-A.03OC_3 | 1630-PM-605A_I_A | 1630-PM-605A - R-101 Recycle Pumps_Phase A current | A | 0..60 |  |  |  |  | 1 | Permanent | 4 | 4 | Read | 32-Bit Floating | 03
4 | 2202-NK-SG-102-A.03OC_4 | 1130-PM-305A_I_A | 1130-PM-305A - HP Flare K.O.Drum Pump_Phase A current | A | 0..30 |  |  |  |  | 1 | Permanent | 4 | 6 | Read | 32-Bit Floating | 03
5 | 2202-NK-SG-102-A.03OC_5 | 1130-PM-306A_I_A | 1130-PM-306A - HP Flare K.O.Drum Pump_Phase A current | A | 0..88 |  |  |  |  | 1 | Permanent | 4 | 8 | Read | 32-Bit Floating | 03
6 | 2202-NK-SG-102-A.03OC_6 | 1162-PM-602_I_A | 1162-PM-602 - HP Flare K.O.Drum Pump_Phase A current | A | 0..60 |  |  |  |  | 1 | Permanent | 4 | 10 | Read | 32-Bit Floating | 03
7 | 2202-NK-SG-102-A.03OC_7 | 1162-PM-603_I_A | 1162-PM-603 - LP Flare K.O.Drum Pump_Phase A current | A | 0..60 |  |  |  |  | 1 | Permanent | 4 | 12 | Read | 32-Bit Floating | 03
8 | 2202-NK-SG-102-A.03OC_8 | 2202-NK-SG-102-A.03OC_8_I_A | 2202-NK-SG-102-A.03OC_8 - LP Flare K.O.Drum Pump_Phase A current | A | 0..6 |  |  |  |  | 1 | Permanent | 4 | 14 | Read | 32-Bit Floating | 03
9 | 2202-NK-SG-102-A.05OC_1 | 1130-PM-311_I_A | 1130-PM-311 - LP Flare K.O.Drum Pump_Phase A current | A | 0..88 |  |  |  |  | 1 | Permanent | 4 | 16 | Read | 32-Bit Floating | 03
10 | 2202-NK-SG-102-A.05OC_2 | 1612-PM-611A_I_A | 1612-PM-611A - Offgas Absorber Bottom Pump_Phase A current | A | 0..120 |  |  |  |  | 1 | Permanent | 4 | 18 | Read | 32-Bit Floating | 03
11 | 2202-NK-SG-102-A.05OC_3 | 1612-PM-001A_I_A | 1612-PM-001A - Offgas Absorber Bottom Pump_Phase A current | A | 0..4.4 |  |  |  |  | 1 | Permanent | 4 | 20 | Read | 32-Bit Floating | 03
12 | 2202-NK-SG-102-A.05OC_4 | 1612-P-611A.HE-JB_I_A | 1612-P-611A.HE-JB - Offgas Absorber Bottom Pump_Phase A current | A | 0..4.4 |  |  |  |  | 1 | Permanent | 4 | 22 | Read | 32-Bit Floating | 03
13 | 2202-NK-SG-102-A.05OC_5 | 1624-PM-614_I_A | 1624-PM-614 - Rich Oil Stripper Bottom Pump_Phase A current | A | 0..74 |  |  |  |  | 1 | Permanent | 4 | 24 | Read | 32-Bit Floating | 03
14 | 2202-NK-SG-102-A.05OC_6 | 2202-NK-SG-102-A.05OC_6_I_A | 2202-NK-SG-102-A.05OC_6 - Rich Oil Stripper Bottom Pump_Phase A current | A | 0..44 |  |  |  |  | 1 | Permanent | 4 | 26 | Read | 32-Bit Floating | 03
15 | 2202-NK-SG-102-A.05OC_7 | 1130-PM-302A_I_A | 1130-PM-302A - SM Slop Drum water Pump_Phase A current | A | 0..148 |  |  |  |  | 1 | Permanent | 4 | 28 | Read | 32-Bit Floating | 03
16 | 2202-NK-SG-102-A.07OC_1 | 1110-KM-101A-2_I_A | 1110-KM-101A-2 - SM Slop Drum water Pump_Phase A current | A | 0..12 |  |  |  |  | 1 | Permanent | 4 | 30 | Read | 32-Bit Floating | 03
17 | 2202-NK-SG-102-A.07OC_2 | 1110-PM-131A_I_A | 1110-PM-131A - SM Slop Drum water Pump_Phase A current | A | 0..16 |  |  |  |  | 1 | Permanent | 4 | 32 | Read | 32-Bit Floating | 03
18 | 2202-NK-SG-102-A.07OC_3 | 1110-PM-131B_I_A | 1110-PM-131B - SM Slop Drum HC Pump_Phase A current | A | 0..16 |  |  |  |  | 1 | Permanent | 4 | 34 | Read | 32-Bit Floating | 03
19 | 2202-NK-SG-102-A.07OC_4 | 1110-KM-101A.EH02_I_A | 1110-KM-101A.EH02 - SM Slop Drum HC Pump_Phase A current | A | 0..16 |  |  |  |  | 1 | Permanent | 4 | 36 | Read | 32-Bit Floating | 03
20 | 2202-NK-SG-102-A.07OC_5 | 1110-PM-133A_I_A | 1110-PM-133A - SM Slop Drum HC Pump_Phase A current | A | 0..30 |  |  |  |  | 1 | Permanent | 4 | 38 | Read | 32-Bit Floating | 03
21 | 2202-NK-SG-102-A.07OC_6 | 1110-V-136.EH_I_A | 1110-V-136.EH - SPARE_Phase A current | A | 0..32 |  |  |  |  | 1 | Permanent | 4 | 40 | Read | 32-Bit Floating | 03
22 | 2202-NK-SG-102-A.07OC_7 | 1130-KM-301A_I_A | 1130-KM-301A - SPARE_Phase A current | A | 0..4.4 |  |  |  |  | 1 | Permanent | 4 | 42 | Read | 32-Bit Floating | 03
23 | 2202-NK-SG-102-A.07OC_8 | 2202-NK-SG-102-A.07OC_8_I_A | 2202-NK-SG-102-A.07OC_8 - SPARE_Phase A current | A | 0..88 |  |  |  |  | 1 | Permanent | 4 | 44 | Read | 32-Bit Floating | 03
24 | 2202-NK-SG-102-A.09OC_1 | 1130-BLM-331A_I_A | 1130-BLM-331A - Back-washed pump_Phase A current | A | 0..16 |  |  |  |  | 1 | Permanent | 4 | 46 | Read | 32-Bit Floating | 03
25 | 2202-NK-SG-102-A.09OC_2 | 1130-PM-331B_I_A | 1130-PM-331B - Back-washed pump_Phase A current | A | 0..180 |  |  |  |  | 1 | Permanent | 4 | 48 | Read | 32-Bit Floating | 03
26 | 2202-NK-SG-102-A.09OC_3 | 1130-V-332A.EH_I_A | 1130-V-332A.EH - Back-washed pump_Phase A current | A | 0..160 |  |  |  |  | 1 | Permanent | 4 | 50 | Read | 32-Bit Floating | 03
27 | 2202-NK-SG-102-A.09OC_4 | 1130-PM-331A_I_A | 1130-PM-331A - Desuperheater Water Pump_Phase A current | A | 0..180 |  |  |  |  | 1 | Permanent | 4 | 52 | Read | 32-Bit Floating | 03
28 | 2202-NK-SG-102-A.11OC_3 | 2701-PK-1501A-M_I_A | 2701-PK-1501A-M - Desuperheater Water Pump_Phase A current | A | 0..2.2 |  |  |  |  | 1 | Permanent | 4 | 54 | Read | 32-Bit Floating | 03
29 | 2202-NK-SG-102-A.11OC_4 | 2701-PM-1215_I_A | 2701-PM-1215 - oil pump motor_Phase A current | A | 0..16 |  |  |  |  | 1 | Permanent | 4 | 56 | Read | 32-Bit Floating | 03
30 | 2202-NK-SG-102-A.11OC_5 | 2701-PM-1701A_I_A | 2701-PM-1701A - oil pump motor_Phase A current | A | 0..4.4 |  |  |  |  | 1 | Permanent | 4 | 58 | Read | 32-Bit Floating | 03
31 | 2202-NK-SG-102-A.11OC_6 | 2701-AGM-1701_I_A | 2701-AGM-1701 - oil pump motor_Phase A current | A | 0..8.8 |  |  |  |  | 1 | Permanent | 4 | 60 | Read | 32-Bit Floating | 03
32 | 2202-NK-SG-102-A.11OC_7 | 2701-PM-1206A_I_A | 2701-PM-1206A - Oil heater junction box_Phase A current | A | 0..180 |  |  |  |  | 1 | Permanent | 4 | 62 | Read | 32-Bit Floating | 03
33 | 2202-NK-SG-102-A.11OC_8 | 2202-NK-SG-102-A.11OC_8_I_A | 2202-NK-SG-102-A.11OC_8 - Oil heater junction box_Phase A current | A | 0..180 |  |  |  |  | 1 | Permanent | 4 | 64 | Read | 32-Bit Floating | 03
34 | 2202-NK-SG-102-A.15OC_1 | 1130-PM-301A_I_A | 1130-PM-301A - Oil heater junction box_Phase A current | A | 0..220 |  |  |  |  | 1 | Permanent | 4 | 66 | Read | 32-Bit Floating | 03
35 | 2202-NK-SG-102-A.15OC_2 | 1130-PM-303A_I_A | 1130-PM-303A - Wasteoil Sump Pump_Phase A current | A | 0..300 |  |  |  |  | 1 | Permanent | 4 | 68 | Read | 32-Bit Floating | 03
36 | 2202-NK-SG-102-A.15OC_3 | 1612-PM-606A_I_A | 1612-PM-606A - Wasteoil Sump Pump_Phase A current | A | 0..300 |  |  |  |  | 1 | Permanent | 4 | 70 | Read | 32-Bit Floating | 03
37 | 2202-NK-SG-102-A.17OC_1 | 2701-PM-1202A_I_A | 2701-PM-1202A - Wasteoil Sump Pump_Phase A current | A | 0..220 |  |  |  |  | 1 | Permanent | 4 | 72 | Read | 32-Bit Floating | 03
38 | 2202-NK-SG-102-A.17OC_2 | 2701-PM-1201A_I_A | 2701-PM-1201A - SPARE_Phase A current | A | 0..300 |  |  |  |  | 1 | Permanent | 4 | 74 | Read | 32-Bit Floating | 03
39 | 2202-NK-SG-102-A.17OC_3 | 2701-PM-1204A_I_A | 2701-PM-1204A - SPARE_Phase A current | A | 0..360 |  |  |  |  | 1 | Permanent | 4 | 76 | Read | 32-Bit Floating | 03
40 | 2202-NK-SG-102-A.19OC_1 | 2701-PM-1203_I_A | 2701-PM-1203 - Process Condensate Pump_Phase A current | A | 0..220 |  |  |  |  | 1 | Permanent | 4 | 78 | Read | 32-Bit Floating | 03
41 | 2202-NK-SG-102-A.19OC_2 | 2701-PM-1207A_I_A | 2701-PM-1207A - Process Condensate Pump_Phase A current | A | 0..220 |  |  |  |  | 1 | Permanent | 4 | 80 | Read | 32-Bit Floating | 03
42 | 2202-NK-SG-102-A.19OC_3 | 2701-PM-1205B_I_A | 2701-PM-1205B - Process Condensate Pump_Phase A current | A | 0..528 |  |  |  |  | 1 | Permanent | 4 | 82 | Read | 32-Bit Floating | 03
43 | 2202-NK-SG-102-A.23OC_1 | 2701-PK-1201A-M_OP_F | 2701-PK-1201A-M - Oil pump motor 1_Operating Frequency | Hz | 0..65 |  |  |  |  | 1 | Permanent | 4 | 84 | Read | 32-Bit Floating | 03
44 | 2202-NK-SG-102-A.23OC_1 | 2701-PK-1201A-M_OUT_CUR | 2701-PK-1201A-M - Oil pump motor 1_Output Current | A | 0..60 |  |  |  |  | 1 | Permanent | 4 | 86 | Read | 32-Bit Floating | 03
45 | 2202-NK-SG-102-B.06OC_1 | 1115-PM-101B_I_A | 1115-PM-101B - Oil pump motor 1_Phase A current | A | 0..88 |  |  |  |  | 1 | Permanent | 4 | 88 | Read | 32-Bit Floating | 03
46 | 2202-NK-SG-102-B.06OC_2 | 1630-PM-214B_I_A | 1630-PM-214B - Oil pump motor 1_Phase A current | A | 0..44 |  |  |  |  | 1 | Permanent | 4 | 90 | Read | 32-Bit Floating | 03
47 | 2202-NK-SG-102-B.06OC_3 | 1630-PM-605B_I_A | 1630-PM-605B - Oil pump motor 2_Phase A current | A | 0..60 |  |  |  |  | 1 | Permanent | 4 | 92 | Read | 32-Bit Floating | 03
48 | 2202-NK-SG-102-B.06OC_4 | 1130-PM-305B_I_A | 1130-PM-305B - Oil pump motor 2_Phase A current | A | 0..30 |  |  |  |  | 1 | Permanent | 4 | 94 | Read | 32-Bit Floating | 03
49 | 2202-NK-SG-102-B.06OC_5 | 1130-PM-306B_I_A | 1130-PM-306B - Oil pump motor 2_Phase A current | A | 0..88 |  |  |  |  | 1 | Permanent | 4 | 96 | Read | 32-Bit Floating | 03
50 | 2202-NK-SG-102-B.06OC_6 | 1130-BLM-331B_I_A | 1130-BLM-331B - Electric heater for crankcase_Phase A current | A | 0..16 |  |  |  |  | 1 | Permanent | 4 | 98 | Read | 32-Bit Floating | 03
51 | 2202-NK-SG-102-B.06OC_7 | 1130-PM-302B_I_A | 1130-PM-302B - Electric heater for crankcase_Phase A current | A | 0..148 |  |  |  |  | 1 | Permanent | 4 | 100 | Read | 32-Bit Floating | 03
52 | 2202-NK-SG-102-B.08OC_1 | 1612-PM-611B_I_A | 1612-PM-611B - Electric heater for crankcase_Phase A current | A | 0..120 |  |  |  |  | 1 | Permanent | 4 | 102 | Read | 32-Bit Floating | 03
53 | 2202-NK-SG-102-B.08OC_2 | 1612-PM-001B_I_A | 1612-PM-001B - Water pump motor 1_Phase A current | A | 0..4.4 |  |  |  |  | 1 | Permanent | 4 | 104 | Read | 32-Bit Floating | 03
54 | 2202-NK-SG-102-B.08OC_3 | 1612-P-611B.HE-JB_I_A | 1612-P-611B.HE-JB - Water pump motor 1_Phase A current | A | 0..4.4 |  |  |  |  | 1 | Permanent | 4 | 106 | Read | 32-Bit Floating | 03
55 | 2202-NK-SG-102-B.08OC_4 | 1110-KM-101B-2_I_A | 1110-KM-101B-2 - Electric heater for water tank_Phase A current | A | 0..12 |  |  |  |  | 1 | Permanent | 4 | 108 | Read | 32-Bit Floating | 03
56 | 2202-NK-SG-102-B.08OC_5 | 1110-PM-132A_I_A | 1110-PM-132A - Electric heater for water tank_Phase A current | A | 0..16 |  |  |  |  | 1 | Permanent | 4 | 110 | Read | 32-Bit Floating | 03
57 | 2202-NK-SG-102-B.08OC_6 | 1110-PM-132B_I_A | 1110-PM-132B - Electric heater for water tank_Phase A current | A | 0..16 |  |  |  |  | 1 | Permanent | 4 | 112 | Read | 32-Bit Floating | 03
58 | 2202-NK-SG-102-B.08OC_7 | 1110-KM-101B.EH02_I_A | 1110-KM-101B.EH02 - Barring motor_Phase A current | A | 0..16 |  |  |  |  | 1 | Permanent | 4 | 114 | Read | 32-Bit Floating | 03
59 | 2202-NK-SG-102-B.08OC_8 | 2202-NK-SG-102-B.08OC_8_I_A | 2202-NK-SG-102-B.08OC_8 - Barring motor_Phase A current | A | 0..6 |  |  |  |  | 1 | Permanent | 4 | 116 | Read | 32-Bit Floating | 03
60 | 2202-NK-SG-102-B.10OC_1 | 1110-PM-133B_I_A | 1110-PM-133B - Barring motor_Phase A current | A | 0..30 |  |  |  |  | 1 | Permanent | 4 | 118 | Read | 32-Bit Floating | 03
61 | 2202-NK-SG-102-B.10OC_2 | 1130-KM-301B_I_A | 1130-KM-301B - SPARE_Phase A current | A | 0..4.4 |  |  |  |  | 1 | Permanent | 4 | 120 | Read | 32-Bit Floating | 03
62 | 2202-NK-SG-102-B.10OC_3 | 1130-PM-332A_I_A | 1130-PM-332A - SPARE_Phase A current | A | 0..180 |  |  |  |  | 1 | Permanent | 4 | 122 | Read | 32-Bit Floating | 03
63 | 2202-NK-SG-102-B.10OC_4 | 1130-PM-332B_I_A | 1130-PM-332B - SPARE_Phase A current | A | 0..180 |  |  |  |  | 1 | Permanent | 4 | 124 | Read | 32-Bit Floating | 03
64 | 2202-NK-SG-102-B.10OC_5 | 1130-V-332B.EH_I_A | 1130-V-332B.EH - Oil station fans_Phase A current | A | 0..160 |  |  |  |  | 1 | Permanent | 4 | 126 | Read | 32-Bit Floating | 03
65 | 2202-NK-SG-102-B.12OC_1 | 2701-PK-1501B-M_I_A | 2701-PK-1501B-M - Oil station fans_Phase A current | A | 0..2.2 |  |  |  |  | 1 | Permanent | 4 | 128 | Read | 32-Bit Floating | 03
66 | 2202-NK-SG-102-B.12OC_2 | 2701-PM-1216_I_A | 2701-PM-1216 - Oil station fans_Phase A current | A | 0..44 |  |  |  |  | 1 | Permanent | 4 | 130 | Read | 32-Bit Floating | 03
67 | 2202-NK-SG-102-B.12OC_3 | 2202-NK-SG-102-B.12OC_3_I_A | 2202-NK-SG-102-B.12OC_3 - Auxiliary oil pump motor_Phase A current | A | 0..44 |  |  |  |  | 1 | Permanent | 4 | 132 | Read | 32-Bit Floating | 03
68 | 2202-NK-SG-102-B.12OC_4 | 2701-PM-1701B_I_A | 2701-PM-1701B - Auxiliary oil pump motor_Phase A current | A | 0..4.4 |  |  |  |  | 1 | Permanent | 4 | 134 | Read | 32-Bit Floating | 03
69 | 2202-NK-SG-102-B.12OC_5 | 2701-PM-1206B_I_A | 2701-PM-1206B - Lube oil tank heater_Phase A current | A | 0..180 |  |  |  |  | 1 | Permanent | 4 | 136 | Read | 32-Bit Floating | 03
70 | 2202-NK-SG-102-B.12OC_6 | 2202-NK-SG-102-B.12OC_6_I_A | 2202-NK-SG-102-B.12OC_6 - Lube oil tank heater_Phase A current | A | 0..180 |  |  |  |  | 1 | Permanent | 4 | 138 | Read | 32-Bit Floating | 03
71 | 2202-NK-SG-102-B.16OC_1 | 1130-PM-301B_I_A | 1130-PM-301B - Lube oil tank heater_Phase A current | A | 0..220 |  |  |  |  | 1 | Permanent | 4 | 140 | Read | 32-Bit Floating | 03
72 | 2202-NK-SG-102-B.16OC_2 | 1130-PM-303B_I_A | 1130-PM-303B - Main oil pump motor_Phase A current | A | 0..300 |  |  |  |  | 1 | Permanent | 4 | 142 | Read | 32-Bit Floating | 03
73 | 2202-NK-SG-102-B.16OC_3 | 1612-PM-606B_I_A | 1612-PM-606B - Main oil pump motor_Phase A current | A | 0..300 |  |  |  |  | 1 | Permanent | 4 | 144 | Read | 32-Bit Floating | 03
74 | 2202-NK-SG-102-B.18OC_1 | 2701-PM-1202B_I_A | 2701-PM-1202B - Main oil pump motor_Phase A current | A | 0..220 |  |  |  |  | 1 | Permanent | 4 | 146 | Read | 32-Bit Floating | 03
75 | 2202-NK-SG-102-B.18OC_2 | 2701-PM-1201B_I_A | 2701-PM-1201B - ITF Waste Gas FanAcoustic Enclosure Fan_Phase A current | A | 0..300 |  |  |  |  | 1 | Permanent | 4 | 148 | Read | 32-Bit Floating | 03
76 | 2202-NK-SG-102-B.18OC_3 | 2701-PM-1205S_I_A | 2701-PM-1205S - ITF Waste Gas FanAcoustic Enclosure Fan_Phase A current | A | 0..528 |  |  |  |  | 1 | Permanent | 4 | 150 | Read | 32-Bit Floating | 03
77 | 2202-NK-SG-102-B.20OC_2 | 2701-PM-1204B_I_A | 2701-PM-1204B - ITF Waste Gas FanAcoustic Enclosure Fan_Phase A current | A | 0..360 |  |  |  |  | 1 | Permanent | 4 | 152 | Read | 32-Bit Floating | 03
78 | 2202-NK-SG-102-B.20OC_1 | 2701-PM-1207B_I_A | 2701-PM-1207B - Slop Drum HC Pump_Phase A current | A | 0..220 |  |  |  |  | 1 | Permanent | 4 | 154 | Read | 32-Bit Floating | 03
79 | 2202-NK-SG-102-B.20OC_3 | 2701-PM-1205A_I_A | 2701-PM-1205A - Slop Drum HC Pump_Phase A current | A | 0..528 |  |  |  |  | 1 | Permanent | 4 | 156 | Read | 32-Bit Floating | 03
80 | 2202-NK-SG-102-B.22OC_1 | 2701-PK-1201B-M_OP_F | 2701-PK-1201B-M - TBC Solution StorageDrum 2701-V-1701Agitator_Operating Frequency | Hz | 0..65 |  |  |  |  | 1 | Permanent | 4 | 158 | Read | 32-Bit Floating | 03
81 | 2202-NK-SG-102-B.22OC_1 | 2701-PK-1201B-M_OUT_CUR | 2701-PK-1201B-M - TBC Solution StorageDrum 2701-V-1701Agitator_Output Current | A | 0..60 |  |  |  |  | 1 | Permanent | 4 | 160 | Read | 32-Bit Floating | 03

## Register Table Function 06
№ п/п | Функциональное обозначение по проекту Project Functional Designation | Tег ПЛК / Hаименование переменной PLC Tag/Variable Name | Описание переменной Description of the variable | Единицы измерения Units of measurement | Шкала scale | LL | LA | HA | HH | Коэффициенты масштабирования Scaling factors | Тип сигнала (Импульс/Постоянный ) Signal type (Impulse/Permanent) | Тип регистра Register type | Адрес/бит Address/Bit | Тип доступа Access type | Тип данных Data type | Код функции Function code | Канал РСУ DCS channel | Tег РСУ / Hаименование переменной DCS Tag/Name variable | Функции РСУ DCS functions | Примечание note
1 | 2202-NK-SG-102-A.03OC_1 | 1115-PM-101A | 1115-PM-101A R-101 Recycle Pumps : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 0 | Write | 16-Bit Unsigned | 06
2 | 2202-NK-SG-102-A.03OC_2 | 1630-PM-214A | 1630-PM-214A HP Flare K.O.Drum Pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 1 | Write | 16-Bit Unsigned | 06
3 | 2202-NK-SG-102-A.03OC_3 | 1630-PM-605A | 1630-PM-605A LP Flare K.O.Drum Pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 2 | Write | 16-Bit Unsigned | 06
4 | 2202-NK-SG-102-A.03OC_4 | 1130-PM-305A | 1130-PM-305A Offgas Absorber Bottom Pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 3 | Write | 16-Bit Unsigned | 06
5 | 2202-NK-SG-102-A.03OC_5 | 1130-PM-306A | 1130-PM-306A Rich Oil Stripper Bottom Pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 4 | Write | 16-Bit Unsigned | 06
6 | 2202-NK-SG-102-A.03OC_6 | 1162-PM-602 | 1162-PM-602 SM Slop Drum water Pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 5 | Write | 16-Bit Unsigned | 06
7 | 2202-NK-SG-102-A.03OC_7 | 1162-PM-603 | 1162-PM-603 SM Slop Drum HC Pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 6 | Write | 16-Bit Unsigned | 06
8 | 2202-NK-SG-102-A.03OC_8 |  | SPARE : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 7 | Write | 16-Bit Unsigned | 06
9 | 2202-NK-SG-102-A.05OC_1 | 1130-PM-311 | 1130-PM-311 Back-washed pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 8 | Write | 16-Bit Unsigned | 06
10 | 2202-NK-SG-102-A.05OC_2 | 1612-PM-611A | 1612-PM-611A Desuperheater Water Pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 9 | Write | 16-Bit Unsigned | 06
11 | 2202-NK-SG-102-A.05OC_3 | 1612-PM-001A | 1612-PM-001A oil pump motor : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 10 | Write | 16-Bit Unsigned | 06
12 | 2202-NK-SG-102-A.05OC_4 | 1612-P-611A.HE-JB | 1612-P-611A.HE-JB Oil heater junction box : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 11 | Write | 16-Bit Unsigned | 06
13 | 2202-NK-SG-102-A.05OC_5 | 1624-PM-614 | 1624-PM-614 Wasteoil Sump Pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 12 | Write | 16-Bit Unsigned | 06
14 | 2202-NK-SG-102-A.05OC_6 |  | SPARE : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 13 | Write | 16-Bit Unsigned | 06
15 | 2202-NK-SG-102-A.05OC_7 | 1130-PM-302A | 1130-PM-302A Process Condensate Pump : MCU TYPE DOL2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 14 | Write | 16-Bit Unsigned | 06
16 | 2202-NK-SG-102-A.07OC_1 | 1110-KM-101A-2 | 1110-KM-101A-2 Barring motor : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 15 | Write | 16-Bit Unsigned | 06
17 | 2202-NK-SG-102-A.07OC_2 | 1110-PM-131A | 1110-PM-131A Oil pump motor 1 : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 16 | Write | 16-Bit Unsigned | 06
18 | 2202-NK-SG-102-A.07OC_3 | 1110-PM-131B | 1110-PM-131B Oil pump motor 2 : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 17 | Write | 16-Bit Unsigned | 06
19 | 2202-NK-SG-102-A.07OC_4 | 1110-KM-101A.EH02 | 1110-KM-101A.EH02 Electric heater for crankcase : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 18 | Write | 16-Bit Unsigned | 06
20 | 2202-NK-SG-102-A.07OC_5 | 1110-PM-133A | 1110-PM-133A Water pump motor 1 : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 19 | Write | 16-Bit Unsigned | 06
21 | 2202-NK-SG-102-A.07OC_6 | 1110-V-136.EH | 1110-V-136.EH Electric heater for water tank : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 20 | Write | 16-Bit Unsigned | 06
22 | 2202-NK-SG-102-A.07OC_7 | 1130-KM-301A | 1130-KM-301A Barring motor : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 21 | Write | 16-Bit Unsigned | 06
23 | 2202-NK-SG-102-A.07OC_8 |  | SPARE : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 22 | Write | 16-Bit Unsigned | 06
24 | 2202-NK-SG-102-A.09OC_1 | 1130-BLM-331A | 1130-BLM-331A Oil station fans : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 23 | Write | 16-Bit Unsigned | 06
25 | 2202-NK-SG-102-A.09OC_2 | 1130-PM-331B | 1130-PM-331B Auxiliary oil pump motor : MCU TYPE DOL2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 24 | Write | 16-Bit Unsigned | 06
26 | 2202-NK-SG-102-A.09OC_3 | 1130-V-332A.EH | 1130-V-332A.EH Lube oil tank heater : MCU TYPE DOL2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 25 | Write | 16-Bit Unsigned | 06
27 | 2202-NK-SG-102-A.09OC_4 | 1130-PM-331A | 1130-PM-331A Main oil pump motor : MCU TYPE DOL2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 26 | Write | 16-Bit Unsigned | 06
28 | 2202-NK-SG-102-A.11OC_3 | 2701-PK-1501A-M | 2701-PK-1501A-M ITF Waste Gas FanAcoustic Enclosure Fan : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 27 | Write | 16-Bit Unsigned | 06
29 | 2202-NK-SG-102-A.11OC_4 | 2701-PM-1215 | 2701-PM-1215 Slop Drum HC Pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 28 | Write | 16-Bit Unsigned | 06
30 | 2202-NK-SG-102-A.11OC_5 | 2701-PM-1701A | 2701-PM-1701A TBC Solution Dosing pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 29 | Write | 16-Bit Unsigned | 06
31 | 2202-NK-SG-102-A.11OC_6 | 2701-AGM-1701 | 2701-AGM-1701 TBC Solution StorageDrum 2701-V-1701Agitator : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 30 | Write | 16-Bit Unsigned | 06
32 | 2202-NK-SG-102-A.11OC_7 | 2701-PM-1206A | 2701-PM-1206A Benzene-Toluene FractionTransfer Pump : MCU TYPE DOL2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 31 | Write | 16-Bit Unsigned | 06
33 | 2202-NK-SG-102-A.11OC_8 |  | SPARE : MCU TYPE DOL2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 32 | Write | 16-Bit Unsigned | 06
34 | 2202-NK-SG-102-A.SS01_1 | 1130-PM-301A | 1130-PM-301A DM Pump : PLC SSR1:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 33 | Write | 16-Bit Unsigned | 06
35 | 2202-NK-SG-102-A.SS01_1 | 1130-PM-303A | 1130-PM-303A Condensate Stripper Bottom Pump : PLC SSR2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 34 | Write | 16-Bit Unsigned | 06
36 | 2202-NK-SG-102-A.SS01_1 | 1612-PM-606A | 1612-PM-606A LLP Condensate Pump : PLC SSR3:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 35 | Write | 16-Bit Unsigned | 06
37 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1202A | 2701-PM-1202A Ethylbenzene transfer pump : PLC SSR1:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 36 | Write | 16-Bit Unsigned | 06
38 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1201A | 2701-PM-1201A Benzene transfer pump : PLC SSR2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 37 | Write | 16-Bit Unsigned | 06
39 | 2202-NK-SG-102-A.SS03_1 | 2701-PM-1204A | 2701-PM-1204A DM Transfer Pump : PLC SSR3:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 38 | Write | 16-Bit Unsigned | 06
40 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1203 | 2701-PM-1203 Off-Spec EB Transfer Pump : PLC SSR1:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 39 | Write | 16-Bit Unsigned | 06
41 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1207A | 2701-PM-1207A Heavy Tar Loading Pump : PLC SSR2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 40 | Write | 16-Bit Unsigned | 06
42 | 2202-NK-SG-102-A.SS05_1 | 2701-PM-1205B | 2701-PM-1205B SM Transfer Pump : PLC SSR3:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 41 | Write | 16-Bit Unsigned | 06
43 | 2202-NK-SG-102-A.23OC_1 | 2701-PK-1201A-M | 2701-PK-1201A-M ITF Waste Gas Fan : VFD Frequency Setting:Hz | 0.01Hz | [5 empty] | 1 | Impulse | 6 | 42 | Write | 16-Bit Unsigned | 06
44 | 2202-NK-SG-102-A.23OC_1 | 2701-PK-1201A-M | 2701-PK-1201A-M ITF Waste Gas Fan : PLC VFD Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 43 | Write | 16-Bit Unsigned | 06
45 | 2202-NK-SG-102-B.06OC_1 | 1115-PM-101B | 1115-PM-101B R-101 Recycle Pumps : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 44 | Write | 16-Bit Unsigned | 06
46 | 2202-NK-SG-102-B.06OC_2 | 1630-PM-214B | 1630-PM-214B HP Flare K.O.Drum Pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 45 | Write | 16-Bit Unsigned | 06
47 | 2202-NK-SG-102-B.06OC_3 | 1630-PM-605B | 1630-PM-605B LP Flare K.O.Drum Pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 46 | Write | 16-Bit Unsigned | 06
48 | 2202-NK-SG-102-B.06OC_4 | 1130-PM-305B | 1130-PM-305B Offgas Absorber Bottom Pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 47 | Write | 16-Bit Unsigned | 06
49 | 2202-NK-SG-102-B.06OC_5 | 1130-PM-306B | 1130-PM-306B Rich Oil Stripper Bottom Pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 48 | Write | 16-Bit Unsigned | 06
50 | 2202-NK-SG-102-B.06OC_6 | 1130-BLM-331B | 1130-BLM-331B Oil station fans : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 49 | Write | 16-Bit Unsigned | 06
51 | 2202-NK-SG-102-B.06OC_7 | 1130-PM-302B | 1130-PM-302B Process Condensate Pump : MCU TYPE DOL2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 50 | Write | 16-Bit Unsigned | 06
52 | 2202-NK-SG-102-B.08OC_1 | 1612-PM-611B | 1612-PM-611B Desuperheater Water Pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 51 | Write | 16-Bit Unsigned | 06
53 | 2202-NK-SG-102-B.08OC_2 | 1612-PM-001B | 1612-PM-001B oil pump motor : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 52 | Write | 16-Bit Unsigned | 06
54 | 2202-NK-SG-102-B.08OC_3 | 1612-P-611B.HE-JB | 1612-P-611B.HE-JB Oil heater junction box : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 53 | Write | 16-Bit Unsigned | 06
55 | 2202-NK-SG-102-B.08OC_4 | 1110-KM-101B-2 | 1110-KM-101B-2 Barring motor : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 54 | Write | 16-Bit Unsigned | 06
56 | 2202-NK-SG-102-B.08OC_5 | 1110-PM-132A | 1110-PM-132A Oil pump motor 1 : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 55 | Write | 16-Bit Unsigned | 06
57 | 2202-NK-SG-102-B.08OC_6 | 1110-PM-132B | 1110-PM-132B Oil pump motor 2 : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 56 | Write | 16-Bit Unsigned | 06
58 | 2202-NK-SG-102-B.08OC_7 | 1110-KM-101B.EH02 | 1110-KM-101B.EH02 Electric heater for crankcase : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 57 | Write | 16-Bit Unsigned | 06
59 | 2202-NK-SG-102-B.08OC_8 |  | SPARE : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 58 | Write | 16-Bit Unsigned | 06
60 | 2202-NK-SG-102-B.10OC_1 | 1110-PM-133B | 1110-PM-133B Water pump motor 2 : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 59 | Write | 16-Bit Unsigned | 06
61 | 2202-NK-SG-102-B.10OC_2 | 1130-KM-301B | 1130-KM-301B Barring motor : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 60 | Write | 16-Bit Unsigned | 06
62 | 2202-NK-SG-102-B.10OC_3 | 1130-PM-332A | 1130-PM-332A Main oil pump motor : MCU TYPE DOL2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 61 | Write | 16-Bit Unsigned | 06
63 | 2202-NK-SG-102-B.10OC_4 | 1130-PM-332B | 1130-PM-332B Auxiliary oil pump motor : MCU TYPE DOL2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 62 | Write | 16-Bit Unsigned | 06
64 | 2202-NK-SG-102-B.10OC_5 | 1130-V-332B.EH | 1130-V-332B.EH Lube oil tank heater : MCU TYPE DOL2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 63 | Write | 16-Bit Unsigned | 06
65 | 2202-NK-SG-102-B.12OC_1 | 2701-PK-1501B-M | 2701-PK-1501B-M "ITF Waste Gas FanAcoustic Enclosure Fan" : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 64 | Write | 16-Bit Unsigned | 06
66 | 2202-NK-SG-102-B.12OC_2 | 2701-PM-1216 | 2701-PM-1216 Slop Drum Water Pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 65 | Write | 16-Bit Unsigned | 06
67 | 2202-NK-SG-102-B.12OC_3 |  | SPARE : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 66 | Write | 16-Bit Unsigned | 06
68 | 2202-NK-SG-102-B.12OC_4 | 2701-PM-1701B | 2701-PM-1701B TBC Solution Dosing pump : MCU TYPE DOL1: Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 67 | Write | 16-Bit Unsigned | 06
69 | 2202-NK-SG-102-B.12OC_5 | 2701-PM-1206B | 2701-PM-1206B Benzene-Toluene FractionTransfer Pump : MCU TYPE DOL2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 68 | Write | 16-Bit Unsigned | 06
70 | 2202-NK-SG-102-B.12OC_6 |  | SPARE : MCU TYPE DOL2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 69 | Write | 16-Bit Unsigned | 06
71 | 2202-NK-SG-102-B.SS01_1 | 1130-PM-301B | 1130-PM-301B DM Pump : PLC SSR1:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 70 | Write | 16-Bit Unsigned | 06
72 | 2202-NK-SG-102-B.SS01_1 | 1130-PM-303B | 1130-PM-303B Condensate Stripper Bottom Pump : PLC SSR2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 71 | Write | 16-Bit Unsigned | 06
73 | 2202-NK-SG-102-B.SS01_1 | 1612-PM-606B | 1612-PM-606B LLP Condensate Pump : PLC SSR3:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 72 | Write | 16-Bit Unsigned | 06
74 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1202B | 2701-PM-1202B Ethylbenzene transfer pump : PLC SSR1:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 73 | Write | 16-Bit Unsigned | 06
75 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1201B | 2701-PM-1201B Benzene transfer pump : PLC SSR2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 74 | Write | 16-Bit Unsigned | 06
76 | 2202-NK-SG-102-B.SS03_1 | 2701-PM-1204B | 2701-PM-1204B DM Transfer Pump : PLC SSR3:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 75 | Write | 16-Bit Unsigned | 06
77 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1207B | 2701-PM-1207B Heavy Tar Loading Pump : PLC SSR1:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 76 | Write | 16-Bit Unsigned | 06
78 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1205A | 2701-PM-1205A SM Transfer Pump : PLC SSR2:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 77 | Write | 16-Bit Unsigned | 06
79 | 2202-NK-SG-102-B.SS05_1 | 2701-PM-1205S | 2701-PM-1205S SM Transfer Pump : PLC SSR3:Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 78 | Write | 16-Bit Unsigned | 06
80 | 2202-NK-SG-102-B.22OC_1 | 2701-PK-1201B-M | 2701-PK-1201B-M ITF Waste Gas Fan : VFD Frequency Setting:Hz | 0.01Hz | [5 empty] | 1 | Impulse | 6 | 79 | Write | 16-Bit Unsigned | 06
81 | 2202-NK-SG-102-B.22OC_1 | 2701-PK-1201B-M | 2701-PK-1201B-M ITF Waste Gas Fan : PLC VFD Control word Pulse signal :Value:1=Stop,2=Start,32=Reset Soft Starter ,1024=Permit,2048=Ban Permit | [6 empty] | 1 | Impulse | 6 | 80 | Write | 16-Bit Unsigned | 06