## Interface parameters
№ п/п | Тип интерфейса Interface type | Тип протокола Protocol type | Slave станция (Источник данных) Slave Station (Data Source) | Slave ID основной Slave ID main | Slave ID резервный Slave ID back-up | Скорость speed | Бит четности Parity bit | Стоп бит Stop bit | Бит данных Data bit | Реверс reverse | Таймаут timeout | максимальная длина maximum length | Примечание note
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
| ТСР/IP | Modbus TCP |  | Hold | Hold
Столбец 1: Column 1:
Указывается порядковый номер интерфейса Specifies the serial number of the interface
Столбец 2: Column 2:
Указывается тип интерфейса: Specifies the type of interface:
ТСР/IP
или последовательные интерфейсы: or serial interfaces:
RS-485 2-Wire
RS-485 4-Wire
RS-422
Столбец 3: Column 3:
Указывается тип протокола обмена информацией: Specify the type of communication protocol:
OPC
Modbus TCP
Modbus RTU
Modbus ASCII
МЭК 60870-5-103
МЭК 60870-5-104
МЭК 61850-8-1
Столбец 4: Column 4:
Указывается функциональное обозначение позиции ПЛК по проекту Project PLC Item Functional Designation to be specified
Столбец 5: Column 5:
Указывается цифровое значени уникальный адрес устройства, для ТСР/IP = адрес ХХХ.ХХХ.ХХХ.ХХХ / маска сети ХХХ.ХХХ.ХХХ.ХХХ / порт XXX или MB = 0..247 Specify the digital value of the unique device address, for TCP/IP = ХХХ.ХХХ.ХХ.ХХ/network mask ХХХ.ХХ.ХХ.ХХ/port XXX or MB = 0.. 247
Столбец 6: Column 6:
Указывается цифровое значени уникальный адрес резервного устройства, для ТСР/IP = адрес ХХХ.ХХХ.ХХХ.ХХХ / маска сети ХХХ.ХХХ.ХХХ.ХХХ / порт XXX или MB = 0..247 Specify the digital value of the unique address of the standby device, for TCP/IP = address ХХХ.ХХХ.ХХ.ХХ/network mask ХХХ.ХХХ.ХХ/port XXX or MB = 0.. 247
Столбец 7: Column 7:
Заполняется для последовательных интерфейсов значение скорости обмена информацией: 115200, 38400, 19200, 9600, 4800 The communication rate value for serial interfaces is 115200, 38400, 19200, 9600, 4800.
Столбец 8: Column 8:
Заполняется для последовательных интерфейсов режим контроля четности: нет, четный, нечетный Parity check mode is filled for serial interfaces: none, even, odd
Столбец 9: Column 9:
Заполняется для последовательных интерфейсов количество стоповых битов, 1 или 2 Number of stop bits, 1 or 2 is filled for serial interfaces
Столбец 10: Column 10:
Заполняется для последовательных интерфейсов число информационных бит в передаваемых и принимаемых байтах, 7 или 8 The number of information bits in transmitted and received bytes is filled for serial interfaces, 7 or 8
Столбец 11: Column 11:
N - стандартный порядок битов, байтов N is the standard order of bits, bytes
RB - инвертированный порядок байт в регистре, сначала младший байт, затем старший RB - inverted byte order in the register, first the lowest byte, then the highest
RR - инвертированный порядок регистров RR - inverted register order
Столбец 12: Column 12:
Указывается максимальное время ожидания ответа устройства на шине, мс Specifies the maximum time to wait for a device response on the bus, ms
Столбец 13: Column 13:
Указывается максимальное количество регистров, которые можно получить в одном запросе Specifies the maximum number of registers that can be obtained in a single request
Столбец 14: Column 14:
Дополнительная информация. Additional information.

## Register Table
№ п/п | Функциональное обозначение по проекту Project Functional Designation | Tег ПЛК / Hаименование переменной PLC Tag/Variable Name | Описание переменной Description of the variable | Единицы измерения Units of measurement | Шкала scale | LL | LA | HA | HH | Коэффициенты масштабирования Scaling factors | Тип сигнала (Импульс/Постоянный ) Signal type (Impulse/Permanent) | Тип регистра Register type | Адрес/бит Address/Bit | Тип доступа Access type | Тип данных Data type | Код функции Function code | Канал РСУ DCS channel | Tег РСУ / Hаименование переменной DCS Tag/Name variable | Функции РСУ DCS functions | Примечание note
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
Рекомендации системного интегратора по формированию адресного пространства: Recommendations of the system integrator on the formation of the address space:
1) Каждый тип данных (16-Bit Unsigned, 16-Bit Signed, 32-Bit Unsigned, BOOL и т.д.) располагать последовательно (группировать по типам); 1) Each data type (16-Bit Unsigned, 16-Bit Signed, 32-Bit Unsigned, BOOL, etc.) should be arranged sequentially (group by type);
2) Для каждого типа данных (16-Bit Unsigned, 16-Bit Signed, 32-Bit Unsigned, BOOL и т.д.) максимально последовательно присваивать адреса с минимальными пропусками в адресном пространстве группы. 2) For each data type (16-Bit Unsigned, 16-Bit Signed, 32-Bit Unsigned, BOOL, etc.), assign addresses with minimal gaps in the address space of the group as much as possible.
Например (Текущая адресация): For example (Current Addressing):
Tag1 - 16-Bit Unsigned – Адрес 1; Tag1 - 16-Bit Unsigned - Address 1;
Tag2 - 32-Bit Unsigned – Адрес 2; Tag2 - 32-Bit Unsigned - Address 2;
Tag3 - 16-Bit Unsigned – Адрес 3; Tag3 - 16-Bit Unsigned - Address 3;
Tag4 - 32-Bit Unsigned – Адрес 4; Tag4 - 32-Bit Unsigned - Address 4;
Рекомендуемая адресация (2 группы): Recommended addressing (2 groups):
Tag1 - 16-Bit Unsigned – Адрес 1; Tag1 - 16-Bit Unsigned - Address 1
Tag3 - 16-Bit Unsigned – Адрес 2; Tag3 - 16-Bit Unsigned - Address 2;
Tag2 - 32-Bit Unsigned – Адрес 3; Tag2 - 32-Bit Unsigned - Address 3;
Tag4 - 32-Bit Unsigned – Адрес 4; Tag4 - 32-Bit Unsigned - Address 4;
3) Минимизировать количество используемых типов данных (16-Bit Unsigned, 32-Bit Unsigned и т.д.). 3) Minimize the number of data types used (16-Bit Unsigned, 32-Bit Unsigned, etc.).
4) Дискретные параметры предпочтительно компоновать в слова состояний. 4) Discrete parameters are preferably composed into state words.
Столбец 1: Column 1:
Указывается порядковый номер позиции Specify the serial number of the item
Столбец 2: Column 2:
Указывается функциональное обозначение позиции по проекту (согласно P&ID). Specify the functional designation of the project item (according to P&ID).
Столбец 3: Column 3:
Указывается имя тега в соответствии с принятой системой кодирования ПЛК Specify the tag name according to the accepted PLC coding system
Заполнить колонку "Обозначение по проекту" для массивов подсистем, указав наименования приборов (сигналов) в соответствии с P&ID (условные обозначениях). Для сигналов ПЛК, отсутствующих на P&ID (условных обозначениях), указать признак "отсутствует на P&ID". Fill in the column "Design designation" for subsystem arrays, indicating the names of devices (signals) in accordance with P&ID (symbols). For PLC signals that are not on P&ID (legend), specify "missing on P&ID."
Столбец 4: Column 4:
Описание переменной Description of the variable
Для сигналов "Режим управления", "Местный" или "Дистанционный" в описании дать пояснения, что является местным, дистанционным режимами (посты управления по месту, PLC, РСУ). For the signals "Control mode," "Local" or "Remote" in the description, explain what is local, remote modes (local control stations, PLC, DCS).
Столбец 5: Column 5:
Единица измерения Unit of measure
Столбец 6: Column 6:
Указывается минимальное, максимальное значение шкалы прибора в формате мин..макс. Для булевых переменных (0 или 1) при невозможности точной идентификации по описанию или наименованию тега указать конкретную привязку состояний переменной (например "1 - в работе, 0 - останов") Specify the minimum, maximum value of the instrument scale in the format of min.. max. For Boolean variables (0 or 1), if it is not possible to accurately identify the description or name of the tag, specify a specific state binding of the variable (for example, "1 - in operation, 0 - shutdown")
Столбец 7-10: Column 7-10:
Указывается уставки сигнализации Alarm setpoints shall be indicated
Столбец 11: Column 11:
Указывается в формате Смещение/Коэффициент для преобразования величины с фиксированной точкой в целочисленную по формуле: Коэффициент* (величина - Смещение) Specified in the Offset/Factor format to convert a fixed-point quantity to an integer by the formula: Factor * (value - Offset)
Столбец 12: Column 12:
Тип сигнала Импульс/Постоянный (для DO). Указывается для дискретных выходных тегов - постоянный (П) или импульсный (И) Signal type Pulse/Constant (for DO). Specified for discrete output tags - constant (D) or pulse (I)
Столбец 13: Column 13:
Указывается тип регистра, в котором хранится переменная в ПЛК Specifies the type of register in which the variable is stored in the PLC
0 - Coils (реле , булевы величины); 0 - Coils (relays, Boolean values);
1 - Status input (статус входа); 1 - Status input;(Entry status)
3 - Input registers (регистры входа); 3 - Input registers;(Logins)
4 - Holding registers (аналоговые регистры). 4 - Holding registers.(analog registers).
Столбец 14: Column 14:
Адрес внутреннего регистра ПЛК / бит (для слов состояния). Address of the internal PLC register/bit (for status words).
Столбец 15: Column 15:
Указывается тип доступа для переменной ПЛК Specifies the access type for the PLC variable
Read - только чтение; Read - read only;
Write - только запись. Запись из РСУ. Для каждого такого сигнала дать пояснение (например в примечании) в каком случае оператор имеет возможность писать в переменную , а в каком не имеет (Например по сигналу режима управления от ЛСАУ/ управление от РСУ) ; Write - record only. Record from DCS. For each such signal, provide an explanation (e.g. in note) in which case the operator is able to write to a variable and in which one he is not (e.g. by the control mode signal from PLCcontrol from DCS);
Read/Write - чтение и запись. Запись из РСУ. Для каждого такого сигнала дать пояснение (например в примечании)в каком случае оператор имеет возможность писать в переменную , а в каком не имеет (Например по сигналу режима управления от ЛСАУ/ управление от РСУ). Read/Write - read and write. Record from DCS. For each such signal, give an explanation (e.g. note) in which case the operator is able to write to a variable and in which one he is not (e.g. by the control mode signal from PLC/control from DCS).
Столбец 16: Column 16:
Указывается тип данных для переменной ПЛК Specifies the data type for the PLC variable
BOOL (булевы величины);
8-Bit Signed (8-ми битные со знаком);
8-Bit Unsigned (8-ми битные без знака);
16-Bit Signed (16-ти битные со знаком);
16-Bit Unsigned (16-ти битные без знака);
32-Bit Signed (32-х битные со знаком);
32-Bit Unsigned (32-х битные без знака);
32-Bit Floating (32-х битные с плавающей точкой);
64-Bit Floating (64-х битные с плавающей точкой).
Столбец 17: Column 17:
Код функции протокола (определяется поставщиком ПЛК). Protocol function code (defined by PLC vendor).
01 - Чтение значений из регистра флага 01 - Reading values from the flag register
02 - Реле входа считывания 02 - Read Input Relay
03 - Регистр хранения данных считывания 03 - Read Data Storage Register
04 - Регистр ввода считывания 04 - Entry reading Register
05 - Запись значений в регистр флага/ Запись во все регистры флагов 05 - Write values to flag register/Write to all flag registers
06 - Запись в регистр хранения/ Запись всех значений 06 - Register Entry/Record All Values
07 - Считывание специальных регистров флагов 07 - Reading Special Flag Registers
08 - Контроль методом обратной передачи данных 08 - Reverse Data Control
09 - Запись значений в регистр флага/ Запись только в измененные регистры флагов 09 - Write Values to Flag Register/Write to Changed Flag Registers Only
10 - Запись в регистр хранения/ Запись только измененных регистров 10 - Write to Storage Register/Write Changed Registers Only
Столбец 18: Column 18:
Адрес внутреннего канала связи в РСУ DCS Internal Link Address
Столбец 19: Column 19:
Указывается имя тега в соответствии с принятой системой кодирования РСУ Specify the tag name according to the accepted DCS coding system
Столбец 20: Column 20:
A - Сигнал тревоги в РСУ - Аварийные уставки, предусмотренные ПЛК , должны быть включены в стандартные процедуры обработки предупредительного сигнала РСУ, чтобы предоставить индикацию аварии и историю аварий. A - DCS Alarm - PLC Emergency Setpoints shall be included in standard DCS alarm handling procedures to provide alarm indication and alarm history.
D - Дисплей в РСУ - Индикация числовых и аналоговых значений (технологические параметры, уставки, выходы контроллеров), представляет собой: цифровые индикаторы, гистограммы, или флаги для графики. D - Display in DCS - Indication of numerical and analog values (process parameters, setpoints, controller outputs), is: digital indicators, histograms, or flags for graphics.
T - Тренд в РСУ - Трендинг аналоговых параметров в РСУ. Необходимо сконфигурировать тренды за истекший период для этих тэгов. T - DCS Trend - DCS Analog Parameter Trend. You need to configure trends over the past period for these tags.
O - Доступ оператора - Обмен данными ‘O’ между ПЛК и РСУ должен быть сконфигурирован в РСУ так, чтобы команда записи из РСУ (например, данные, которые будут записаны в ПЛК) по интерфейс у была послана после завершения ввода оператора только однажды. Необходимо обеспечить доступ оператора из РСУ так же как с локальной станции (панели) оператора (HMI). В данном режиме должно быть точное понимание о том, кто управляет в данный момент. Дать пояснения доступ оператора возможен только или с РСУ или с ПЛК по сигналу режима управления от ЛСАУ/ от РСУ. O - Operator Access - The "O" data exchange between the PLC and the DCS shall be configured in the DCS so that the write command from the DCS (e.g. data to be written to the PLC) on interface y is sent after the operator input is completed only once. Operator access from the DCS shall be provided as well as from the Local Operator Station (Panel) (HMI). This mode should have an accurate understanding of who is currently managing. Operator access can only be explained either from DCS or PLC by control mode signal from PLC/DCS.
E - Доступ инженера - Обмен данными ‘E’ между ПЛК и РСУ должен быть сконфигурирован в РСУ так, чтобы команда записи из РСУ (например, данные, которые будут записаны в ПЛК) по интерфейс у была послана после завершения ввода оператора только однажды. Необходимо обеспечить доступ инженера из РСУ так же как с локальной станции (панели) оператора (HMI). Доступ к этой функции должен быть защищен паролем и доступен только для инженеров (не должно быть доступно для операторов). В данном режиме должно быть точное понимание о том, кто управляет в данный момент. Дать пояснения доступ инженера возможен только или с РСУ или с ПЛК по сигналу режима управления от ЛСАУ/ от РСУ. E - Engineer Access - Data exchange "E" between PLC and DCS shall be configured in DCS so that write command from DCS (e.g. data to be written to PLC) on interface y is sent after completion of operator input only once. Engineer access from DCS shall be provided as well as from local operator station (panel) (HMI). Access to this feature must be password protected and only available to engineers (not available to operators). This mode should have an accurate understanding of who is currently managing. Only DCS or PLC can provide an explanation of the engineer's access to the control mode signal from PLC/DCS.
W - Непрерывная запись - Обмен данными ‘W’ должен обеспечить непрерывную запись из РСУ в ПЛК. Эта функция применяется для технологических параметров, собранных РСУ и передаваемых в ПЛК через интерфейс . W - Continuous Recording - Data exchange "W" shall ensure continuous recording from DCS to PLC. This function applies to process parameters collected by DCS and transmitted to PLC via interface.
Столбец 21: Column 21:
Дополнительная информация. Additional information.

## Register Table_Slave_AO
№ п/п | Функциональное обозначение по проекту Project Functional Designation | Tег ПЛК / Hаименование переменной PLC Tag/Variable Name | Описание переменной Description of the variable | Единицы измерения Units of measurement | Шкала scale | LL | LA | HA | HH | Коэффициенты масштабирования Scaling factors | Тип сигнала (Импульс/Постоянный ) Signal type (Impulse/Permanent) | Тип регистра Register type | Адрес/бит Address/Bit | Тип доступа Access type | Тип данных Data type | Код функции Function code | Канал РСУ DCS channel | Tег РСУ / Hаименование переменной DCS Tag/Name variable | Функции РСУ DCS functions | Примечание note
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
1 |  | a1130_FT_34101 | Inlet fluid replenishment flow transmitter | kg/h | 0-6100 | - | - | - | - | 1 |  | 3 | 30001 | READ | REAL |  |  |  | A
2 |  | a1130_FT_34501 | Sealing gas flow transmitter | Nm3/h | 0-85 | - | 20 | - | - | 1 |  | 3 | 30003 | READ | REAL |  |  |  | A
3 |  | a1130_FT_34502 | Sealing gas flow transmitter | Nm3/h | 0-85 | - | 20 | - | - | 1 |  | 3 | 30005 | READ | REAL |  |  |  | A
4 |  | a1130_FT_34503 | Sealing gas flow transmitter | Nm3/h | 0-85 | - | 20 | - | - | 1 |  | 3 | 30007 | READ | REAL |  |  |  | A
5 |  | a1130_FT_34504 | Sealing gas flow transmitter | Nm3/h | 0-85 | - | 20 | - | - | 1 |  | 3 | 30009 | READ | REAL |  |  |  | A
6 |  | a1130_LT_34301 | Lubricating oil tank level transmitter | % | 0-100 | - | 50 | - | - | 1 |  | 3 | 30011 | READ | REAL |  |  |  | A
7 |  | a1130_LT_34302 | Run down tank level transmitter | % | 0-100 | - | 80 | - | - | 1 |  | 3 | 30013 | READ | REAL |  |  |  | A
8 |  | a1130_PDT_34101 | Suction line filter differential pressure transmitter | kPa | 0-20 | - | - | 3 | - | 1 |  | 3 | 30015 | READ | REAL |  |  |  | A
9 |  | a1130_PDT_34102 | Inlet fluid replenishment filter differential pressure transmitter | MPa(G) | 0-0.4 | - | - | 0.15 | - | 1 |  | 3 | 30017 | READ | REAL |  |  |  | A
10 |  | a1130_PDT_34301 | Lubricating oil filter differential pressure transmitter | MPa(G) | 0-0.25 | - | - | 0.15 | - | 1 |  | 3 | 30019 | READ | REAL |  |  |  | A
11 |  | a1130_PDT_34501 | Seal nitrogen inlet filter differential pressure transmitter | MPa(G) | 0-0.3 | - | - | 0.1 | - | 1 |  | 3 | 30021 | READ | REAL |  |  |  | A
12 |  | a1130_PDT_34502 | Sealing gas differential pressure transmitter | MPa(G) | 0-0.5 | 0.1 | 0.2 | - | - | 1 |  | 3 | 30023 | READ | REAL |  |  |  | A
13 |  | a1130_PT_34101 | Compressor suction line pressure | kPa(A) | 0-250 | - | 21 | - | - | 1 |  | 3 | 30025 | READ | REAL |  |  |  | A
14 |  | a1130_PT_34102 | Compressor suction line pressure transmitter | kPa(A) | 0-250 | 16 | - | - | - | 1 |  | 3 | 30027 | READ | REAL |  |  |  | A
15 |  | a1130_PT_34103 | Compressor suction line pressure transmitter | kPa(A) | 0-250 | 16 | - | - | - | 1 |  | 3 | 30029 | READ | REAL |  |  |  | A
16 |  | a1130_PT_34104 | Compressor suction line pressure transmitter | kPa(A) | 0-250 | 16 | - | - | - | 1 |  | 3 | 30031 | READ | REAL |  |  |  | A
17 |  | a1130_PT_34105 | Compressor discharge line pressure transmitter | kPa(A) | 0-250 | - | - | 180 | 190 | 1 |  | 3 | 30033 | READ | REAL |  |  |  | A
18 |  | a1130_PT_34106 | Compressor discharge line pressure transmitter | kPa(A) | 0-250 | - | - | 180 | 190 | 1 |  | 3 | 30035 | READ | REAL |  |  |  | A
19 |  | a1130_PT_34107 | Compressor discharge line pressure transmitter | kPa(A) | 0-250 | - | - | 180 | 190 | 1 |  | 3 | 30037 | READ | REAL |  |  |  | A
20 |  | a1130_PT_34301 | Pressure transmitter after lubricating oil filter | MPa(G) | 0-1.6 | - | 0.6 | - | - | 1 |  | 3 | 30039 | READ | REAL |  |  |  | A
21 |  | a1130_PT_34302 | Lubricating oil supply manifold pressure transmitter | MPa(G) | 0-1 | 0.2 | - | - | - | 1 |  | 3 | 30041 | READ | REAL |  |  |  | A
22 |  | a1130_PT_34303 | Lubricating oil supply manifold pressure transmitter | MPa(G) | 0-1 | 0.2 | - | - | - | 1 |  | 3 | 30043 | READ | REAL |  |  |  | A
23 |  | a1130_PT_34304 | Lubricating oil supply manifold pressure transmitter | MPa(G) | 0-1 | 0.2 | - | - | - | 1 |  | 3 | 30045 | READ | REAL |  |  |  | A
24 |  | a1130_PT_34501 | Sealing gas pressure transmitter | MPa(G) | 0-0.5 | - | 0.2 | - | - | 1 |  | 3 | 30047 | READ | REAL |  |  |  | A
25 |  | a1130_PT_35301 | Turbine regulating oil pressure | MPa(G) | 0-1.6 | - | 0.6 | - | - | 1 |  | 3 | 30049 | READ | REAL |  |  |  | A
26 |  | a1130_PT_35501 | Turbine closing oil pressure | MPa(G) | 0-1.6 | - | 0.15 | - | - | 1 |  | 3 | 30051 | READ | REAL |  |  |  | A
27 |  | a1130_PT_35701 | Turbine exhaust pressure transmitter | MPa(G) | 0-1 | 0.325 | 0.375 | 0.475 | - | 1 |  | 3 | 30053 | READ | REAL |  |  |  | A
28 |  | a1130_PT_35702 | Turbine exhaust pressure transmitter | MPa(G) | 0-1 | 0.325 | 0.375 | 0.475 | - | 1 |  | 3 | 30055 | READ | REAL |  |  |  | A
29 |  | a1130_PT_35703 | Turbine exhaust pressure transmitter | MPa(G) | 0-1 | 0.325 | 0.375 | 0.475 | - | 1 |  | 3 | 30057 | READ | REAL |  |  |  | A
30 |  | a1130_TE_34701 | Compressor suction male rotor radial bearing temperature | ℃ | -50-200 | - | - | 80 | 90 | 1 |  | 3 | 30059 | READ | REAL |  |  |  | A
31 |  | a1130_TE_34702 | Compressor suction male rotor radial bearing temperature | ℃ | -50-200 | - | - | 80 | 90 | 1 |  | 3 | 30061 | READ | REAL |  |  |  | A
32 |  | a1130_TE_34703 | Compressor suction female rotor radial bearing temperature | ℃ | -50-200 | - | - | 80 | 90 | 1 |  | 3 | 30063 | READ | REAL |  |  |  | A
33 |  | a1130_TE_34704 | Compressor suction female rotor radial bearing temperature | ℃ | -50-200 | - | - | 80 | 90 | 1 |  | 3 | 30065 | READ | REAL |  |  |  | A
34 |  | a1130_TE_34705 | Compressor discharge male rotor radial bearing temperature | ℃ | -50-200 | - | - | 80 | 90 | 1 |  | 3 | 30067 | READ | REAL |  |  |  | A
35 |  | a1130_TE_34706 | Compressor discharge male rotor radial bearing temperature | ℃ | -50-200 | - | - | 80 | 90 | 1 |  | 3 | 30069 | READ | REAL |  |  |  | A
36 |  | a1130_TE_34707 | Compressor discharge female rotor radial bearing temperature | ℃ | -50-200 | - | - | 80 | 90 | 1 |  | 3 | 30071 | READ | REAL |  |  |  | A
37 |  | a1130_TE_34708 | Compressor discharge female rotor radial bearing temperature | ℃ | -50-200 | - | - | 80 | 90 | 1 |  | 3 | 30073 | READ | REAL |  |  |  | A
38 |  | a1130_TE_34709 | Compressor male rotor thrust bearing temperature | ℃ | -50-200 | - | - | 80 | 90 | 1 |  | 3 | 30075 | READ | REAL |  |  |  | A
39 |  | a1130_TE_34710 | Compressor male rotor thrust bearing temperature | ℃ | -50-200 | - | - | 80 | 90 | 1 |  | 3 | 30077 | READ | REAL |  |  |  | A
40 |  | a1130_TE_34711 | Compressor female rotor thrust bearing temperature | ℃ | -50-200 | - | - | 80 | 90 | 1 |  | 3 | 30079 | READ | REAL |  |  |  | A
41 |  | a1130_TE_34712 | Compressor female rotor thrust bearing temperature | ℃ | -50-200 | - | - | 80 | 90 | 1 |  | 3 | 30081 | READ | REAL |  |  |  | A
42 |  | a1130_TE_34713 | Gear box bearing temperature | ℃ | 0-200 | - | - | 100 | 110 | 1 |  | 3 | 30083 | READ | REAL |  |  |  | A
43 |  | a1130_TE_34714 | Gear box bearing temperature | ℃ | 0-200 | - | - | 100 | 110 | 1 |  | 3 | 30085 | READ | REAL |  |  |  | A
44 |  | a1130_TE_34715 | Gear box bearing temperature | ℃ | 0-200 | - | - | 100 | 110 | 1 |  | 3 | 30087 | READ | REAL |  |  |  | A
45 |  | a1130_TE_34716 | Gear box bearing temperature | ℃ | 0-200 | - | - | 100 | 110 | 1 |  | 3 | 30089 | READ | REAL |  |  |  | A
46 |  | a1130_TE_34717 | Gear box bearing temperature | ℃ | 0-200 | - | - | 100 | 110 | 1 |  | 3 | 30091 | READ | REAL |  |  |  | A
47 |  | a1130_TE_34718 | Gear box bearing temperature | ℃ | 0-200 | - | - | 100 | 110 | 1 |  | 3 | 30093 | READ | REAL |  |  |  | A
48 |  | a1130_TE_34719 | Gear box bearing temperature | ℃ | 0-200 | - | - | 100 | 110 | 1 |  | 3 | 30095 | READ | REAL |  |  |  | A
49 |  | a1130_TE_34720 | Gear box bearing temperature | ℃ | 0-200 | - | - | 100 | 110 | 1 |  | 3 | 30097 | READ | REAL |  |  |  | A
50 |  | a1130_TE_34721 | Turbine bearing temperature | ℃ | 0-200 | - | - | 105 | 115 | 1 |  | 3 | 30099 | READ | REAL |  |  |  | A
51 |  | a1130_TE_34722 | Turbine bearing temperature | ℃ | 0-200 | - | - | 105 | 115 | 1 |  | 3 | 30101 | READ | REAL |  |  |  | A
52 |  | a1130_TE_34723 | Turbine bearing temperature | ℃ | 0-200 | - | - | 105 | 115 | 1 |  | 3 | 30103 | READ | REAL |  |  |  | A
53 |  | a1130_TE_34724 | Turbine bearing temperature | ℃ | 0-200 | - | - | 105 | 115 | 1 |  | 3 | 30105 | READ | REAL |  |  |  | A
54 |  | a1130_TE_34725 | Turbine thrust bearing temperature | ℃ | 0-200 | - | - | 105 | 115 | 1 |  | 3 | 30107 | READ | REAL |  |  |  | A
55 |  | a1130_TE_34726 | Turbine thrust bearing temperature | ℃ | 0-200 | - | - | 105 | 115 | 1 |  | 3 | 30109 | READ | REAL |  |  |  | A
56 |  | a1130_TE_34727 | Turbine thrust bearing temperature | ℃ | 0-200 | - | - | 105 | 115 | 1 |  | 3 | 30111 | READ | REAL |  |  |  | A
57 |  | a1130_TE_34728 | Turbine thrust bearing temperature | ℃ | 0-200 | - | - | 105 | 115 | 1 |  | 3 | 30113 | READ | REAL |  |  |  | A
58 |  | a1130_TT_34101 | Compressor suction line temperature transmitter | ℃ | -50-100 | - | - | 43 | - | 1 |  | 3 | 30115 | READ | REAL |  |  |  | A
59 |  | a1130_TT_34102 | Compressor discharge line temperature transmitter | ℃ | -50-250 | - | - | 155 | - | 1 |  | 3 | 30117 | READ | REAL |  |  |  | A
60 |  | a1130_TT_34103 | Compressor discharge line temperature transmitter | ℃ | -50-250 | - | - | - | 160 | 1 |  | 3 | 30119 | READ | REAL |  |  |  | A
61 |  | a1130_TT_34104 | Compressor discharge line temperature transmitter | ℃ | -50-250 | - | - | - | 160 | 1 |  | 3 | 30121 | READ | REAL |  |  |  | A
62 |  | a1130_TT_34105 | Compressor discharge line temperature transmitter | ℃ | -50-250 | - | - | - | 160 | 1 |  | 3 | 30123 | READ | REAL |  |  |  | A
63 |  | a1130_TT_34301 | Lubricating oil tank temperature transmitter | ℃ | -50-100 | - | 10 | - | - | 1 |  | 3 | 30125 | READ | REAL |  |  |  | A
64 |  | a1130_TT_34302 | Lubricating oil supply manifold temperature transmitter | ℃ | -50-100 | - | 10 | 55 | - | 1 |  | 3 | 30127 | READ | REAL |  |  |  | A
65 |  | a1130_TZT_34101 | Inlet fluid replenishing valve position feedback | % | 0-100 | - | - | - | - | 1 |  | 3 | 30129 | READ | REAL |  |  |  | A
66 |  | a1130_VE_34901 | Compressor bearing vibration | um | 0-200 | - | - | 80 | 120 | 1 |  | 3 | 30131 | READ | REAL |  |  |  | A
67 |  | a1130_VE_34902 | Compressor bearing vibration | um | 0-200 | - | - | 80 | 120 | 1 |  | 3 | 30133 | READ | REAL |  |  |  | A
68 |  | a1130_VE_34903 | Compressor bearing vibration | um | 0-200 | - | - | 80 | 120 | 1 |  | 3 | 30135 | READ | REAL |  |  |  | A
69 |  | a1130_VE_34904 | Compressor bearing vibration | um | 0-200 | - | - | 80 | 120 | 1 |  | 3 | 30137 | READ | REAL |  |  |  | A
70 |  | a1130_VE_34905 | Compressor bearing vibration | um | 0-200 | - | - | 80 | 120 | 1 |  | 3 | 30139 | READ | REAL |  |  |  | A
71 |  | a1130_VE_34906 | Compressor bearing vibration | um | 0-200 | - | - | 80 | 120 | 1 |  | 3 | 30141 | READ | REAL |  |  |  | A
72 |  | a1130_VE_34907 | Compressor bearing vibration | um | 0-200 | - | - | 80 | 120 | 1 |  | 3 | 30143 | READ | REAL |  |  |  | A
73 |  | a1130_VE_34908 | Compressor bearing vibration | um | 0-200 | - | - | 80 | 120 | 1 |  | 3 | 30145 | READ | REAL |  |  |  | A
74 |  | a1130_VE_34909 | Gear box bearing vibration | um | 0-200 | - | - | 80 | 100 | 1 |  | 3 | 30147 | READ | REAL |  |  |  | A
75 |  | a1130_VE_34910 | Gear box bearing vibration | um | 0-200 | - | - | 80 | 100 | 1 |  | 3 | 30149 | READ | REAL |  |  |  | A
76 |  | a1130_VE_34911 | Gear box bearing vibration | um | 0-200 | - | - | 70 | 90 | 1 |  | 3 | 30151 | READ | REAL |  |  |  | A
77 |  | a1130_VE_34912 | Gear box bearing vibration | um | 0-200 | - | - | 70 | 90 | 1 |  | 3 | 30153 | READ | REAL |  |  |  | A
78 |  | a1130_VE_34913 | Gear box bearing vibration | um | 0-200 | - | - | 80 | 100 | 1 |  | 3 | 30155 | READ | REAL |  |  |  | A
79 |  | a1130_VE_34914 | Gear box bearing vibration | um | 0-200 | - | - | 80 | 100 | 1 |  | 3 | 30157 | READ | REAL |  |  |  | A
80 |  | a1130_VE_34915 | Gear box bearing vibration | um | 0-200 | - | - | 80 | 100 | 1 |  | 3 | 30159 | READ | REAL |  |  |  | A
81 |  | a1130_VE_34916 | Gear box bearing vibration | um | 0-200 | - | - | 80 | 100 | 1 |  | 3 | 30161 | READ | REAL |  |  |  | A
82 |  | a1130_VE_34917 | Turbine bearing vibration | um | 0-200 | - | - | 80 | 100 | 1 |  | 3 | 30163 | READ | REAL |  |  |  | A
83 |  | a1130_VE_34918 | Turbine bearing vibration | um | 0-200 | - | - | 80 | 100 | 1 |  | 3 | 30165 | READ | REAL |  |  |  | A
84 |  | a1130_VE_34919 | Turbine bearing vibration | um | 0-200 | - | - | 80 | 100 | 1 |  | 3 | 30167 | READ | REAL |  |  |  | A
85 |  | a1130_VE_34920 | Turbine bearing vibration | um | 0-200 | - | - | 80 | 100 | 1 |  | 3 | 30169 | READ | REAL |  |  |  | A
86 |  | a1130_ZE_34901 | Compressor thrust bearing displacement | mm | -1-1 | -0.4 | -0.3 | 0.3 | 0.4 | 1 |  | 3 | 30171 | READ | REAL |  |  |  | A
87 |  | a1130_ZE_34902 | Compressor thrust bearing displacement | mm | -1-1 | -0.4 | -0.3 | 0.3 | 0.4 | 1 |  | 3 | 30173 | READ | REAL |  |  |  | A
88 |  | a1130_ZE_34903 | Compressor thrust bearing displacement | mm | -1-1 | -0.4 | -0.3 | 0.3 | 0.4 | 1 |  | 3 | 30175 | READ | REAL |  |  |  | A
89 |  | a1130_ZE_34904 | Compressor thrust bearing displacement | mm | -1-1 | -0.4 | -0.3 | 0.3 | 0.4 | 1 |  | 3 | 30177 | READ | REAL |  |  |  | A
90 |  | a1130_ZE_34905 | Turbine displacement | mm | -1-1 | -0.8 | -0.56 | 0.56 | 0.8 | 1 |  | 3 | 30179 | READ | REAL |  |  |  | A
91 |  | a1130_ZE_34906 | Turbine displacement | mm | -1-1 | -0.8 | -0.56 | 0.56 | 0.8 | 1 |  | 3 | 30181 | READ | REAL |  |  |  | A
92 |  | p1130_SE_35501 | Turbine speed sensor | RPM | 0-15000 | - | - | - | - | 1 |  | 3 | 30183 | READ | REAL |  |  |  | A
93 |  | p1130_SE_35502 | Turbine speed sensor | RPM | 0-15000 | - | - | - | - | 1 |  | 3 | 30185 | READ | REAL |  |  |  | A
94 |  | p1130_SE_35503 | Turbine speed sensor | RPM | 0-15000 | - | - | - | 13608 | 1 |  | 3 | 30187 | READ | REAL |  |  |  | A
95 |  | p1130_SE_35504 | Turbine speed sensor | RPM | 0-15000 | - | - | - | 13608 | 1 |  | 3 | 30189 | READ | REAL |  |  |  | A
96 |  | p1130_SE_35505 | Turbine speed sensor | RPM | 0-15000 | - | - | - | 13608 | 1 |  | 3 | 30191 | READ | REAL |  |  |  | A
97 |  | y1130_TGV_35501_HA | Electro-hydraulic converter signal given | % | 0-100 | - | - | - | - | 1 |  | 3 | 30193 | READ | REAL |  |  |  | D
98 |  | y1130_TV_34101 | Inlet fluid replenishing valve(FO) | % | 0-100 | - | - | - | - | 1 |  | 3 | 30195 | READ | REAL |  |  |  | D
99 |  | r1130_VPE_34901 | Turbine key phasor | [6 empty] | 1 |  | 3 | 30197 | READ | REAL |  |  |  | D
100 |  | r1130_VPE_34902 | Gearbox key phase preamplifier | [6 empty] | 1 |  | 3 | 30199 | READ | REAL |  |  |  | D
101 |  | r1130_FT_34101_DP | Inlet fluid replenishment flow transmitter DP | [6 empty] | 1 |  | 3 | 30201 | READ | REAL |  |  |  | D
102 |  | rFlow1_DB_1A1 | PID adjust deadband | [6 empty] | 1 |  | 3 | 30203 | READ | REAL |  |  |  | D
103 |  | rFlow1_KPB_1A1 | PID Gain | [6 empty] | 1 |  | 3 | 30205 | READ | REAL |  |  |  | D
104 |  | rFlow1_RESET_1A1 | PID Reset | [6 empty] | 1 |  | 3 | 30207 | READ | REAL |  |  |  | D
105 |  | rPEKSPDREC_1A1 | Governor-peak speed | [6 empty] | 1 |  | 3 | 30209 | READ | REAL |  |  |  | D
106 |  | rPU1_1A1 | Governor- speed sensor1 | [6 empty] | 1 |  | 3 | 30211 | READ | REAL |  |  |  | D
107 |  | rPU2_1A1 | Governor- speed sensor2 | [6 empty] | 1 |  | 3 | 30213 | READ | REAL |  |  |  | D
108 |  | rPress1_DB_1A1 | PID adjust deadband | [6 empty] | 1 |  | 3 | 30215 | READ | REAL |  |  |  | D
109 |  | rPress1_KPB_1A1 | PID Gain | [6 empty] | 1 |  | 3 | 30217 | READ | REAL |  |  |  | D
110 |  | rPress1_RESET_1A1 | PID Reset | [6 empty] | 1 |  | 3 | 30219 | READ | REAL |  |  |  | D
111 |  | rSIC_OUT_1A1 | Governor- speed control out | [6 empty] | 1 |  | 3 | 30221 | READ | REAL |  |  |  | D
112 |  | rSIC_PB_1A1 | Governor- speed PID Gain | [6 empty] | 1 |  | 3 | 30223 | READ | REAL |  |  |  | D
113 |  | rSIC_RESET_1A1 | Governor- speed PID Reset | [6 empty] | 1 |  | 3 | 30225 | READ | REAL |  |  |  | D
114 |  | rSPDSP_1A1 | Governor- speed setpoint | [6 empty] | 1 |  | 3 | 30227 | READ | REAL |  |  |  | D
115 |  | rSPDTARG_1A1 | Governor- speed target | [6 empty] | 1 |  | 3 | 30229 | READ | REAL |  |  |  | D
116 |  | rSPEED_1A1 | Governor-Turbine speed | [6 empty] | 1 |  | 3 | 30231 | READ | REAL |  |  |  | D
117 |  | rTD1_1A1 | Governor-1st stage warm up count down | [6 empty] | 1 |  | 3 | 30233 | READ | REAL |  |  |  | D
118 |  | rTRPSPDREC_1A1 | Governor-Trip speed | [6 empty] | 1 |  | 3 | 30235 | READ | REAL |  |  |  | D
119 |  | rTemp1_DB_1A1 | PID Deadband | [6 empty] | 1 |  | 3 | 30237 | READ | REAL |  |  |  | D
120 |  | rTemp1_KPB_1A1 | PID Gain | [6 empty] | 1 |  | 3 | 30239 | READ | REAL |  |  |  | D
121 |  | rTemp1_RESET_1A1 | PID Reset | [6 empty] | 1 |  | 3 | 30241 | READ | REAL |  |  |  | D
122 |  | yFlow1_OUT_1A1 | PID out | [6 empty] | 1 |  | 3 | 30243 | READ | REAL |  |  |  | D
123 |  | yPress1_OUT_1A1 | PID out | [6 empty] | 1 |  | 3 | 30245 | READ | REAL |  |  |  | D
124 |  | yTemp1_OUT_1A1 | PID out | [6 empty] | 1 |  | 3 | 30247 | READ | REAL |  |  |  | D
125 |  | iMODE_1A1 | Governor-raise mode | [6 empty] | 1 |  | 3 | 30249 | READ | REAL |  |  |  | D
126 |  | iFIFO_NUM_1A1 | First Out number | [6 empty] | 1 |  | 3 | 30251 | READ | REAL |  |  |  | D
127 |  | kMAXSPD_1A1 | Governor- maximum controllable speed | [6 empty] | 1 |  | 3 | 30253 | READ | REAL |  |  |  | D
128 |  | kMINSPD_1A1 | Governor- minimum controllable speed | [6 empty] | 1 |  | 3 | 30255 | READ | REAL |  |  |  | D
129 |  | kOST_E_1A1 | Governor-electronic overspeed value | [6 empty] | 1 |  | 3 | 30257 | READ | REAL |  |  |  | D
130 |  | kOST_M_1A1 | Governor-Machenical overspeed value | [6 empty] | 1 |  | 3 | 30259 | READ | REAL |  |  |  | D
131 |  | kRR_7_1A1 | Governor- raise speed rate | [6 empty] | 1 |  | 3 | 30261 | READ | REAL |  |  |  | D
132 |  | kWM1_RATE_1A1 | Governor-1st stage warm up raise speed rate | [6 empty] | 1 |  | 3 | 30263 | READ | REAL |  |  |  | D
133
134
135
136
137
138
139
140
141
142
143

## Register Table_Slave_AI
№ п/п | Функциональное обозначение по проекту Project Functional Designation | Tег ПЛК / Hаименование переменной PLC Tag/Variable Name | Описание переменной Description of the variable | Единицы измерения Units of measurement | Шкала scale | LL | LA | HA | HH | Коэффициенты масштабирования Scaling factors | Тип сигнала (Импульс/Постоянный ) Signal type (Impulse/Permanent) | Тип регистра Register type | Адрес/бит Address/Bit | Тип доступа Access type | Тип данных Data type | Код функции Function code | Канал РСУ DCS channel | Tег РСУ / Hаименование переменной DCS Tag/Name variable | Функции РСУ DCS functions | Примечание note
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
1 |  | eFlow1_KPB_1A1_D | PID Gain from DCS | [6 empty] | 1 |  | 4 | 40001 | Write | REAL |  |  |  | E
2 |  | eFlow1_MSP_1A1_D | PID manual value from DCS | [6 empty] | 1 |  |  | 40003 | Write | REAL |  |  |  | O
3 |  | eFlow1_RESET_1A1_D | PID Reset from DCS | [6 empty] | 1 |  |  | 40005 | Write | REAL |  |  |  | E
4 |  | eFlow1_SP_1A1_D | PID setpoint from DCS | [6 empty] | 1 |  |  | 40007 | Write | REAL |  |  |  | O
5 |  | ePress1_KPB_1A1_D | PID Gain from DCS | [6 empty] | 1 |  |  | 40009 | Write | REAL |  |  |  | E
6 |  | ePress1_MSP_1A1_D | PID manual value from DCS | [6 empty] | 1 |  |  | 40011 | Write | REAL |  |  |  | O
7 |  | ePress1_RESET_1A1_D | PID Reset from DCS | [6 empty] | 1 |  |  | 40013 | Write | REAL |  |  |  | E
8 |  | ePress1_SP_1A1_D | PID setpoint from DCS | [6 empty] | 1 |  |  | 40015 | Write | REAL |  |  |  | O
9 |  | eSIC_PID_PB_1A1_D | Governor- speed controlPID Gain from DCS | [6 empty] | 1 |  |  | 40017 | Write | REAL |  |  |  | E
10 |  | eSIC_PID_RESET_1A1_D | Governor- speed controlPID Reset from DCS | [6 empty] | 1 |  |  | 40019 | Write | REAL |  |  |  | E
11 |  | eSPDSPT_1A1_D | Governor- target speed from DCS | [6 empty] | 1 |  |  | 40021 | Write | REAL |  |  |  | O
12 |  | eTemp1_KPB_1A1_D | PID Gain from DCS | [6 empty] | 1 |  |  | 40023 | Write | REAL |  |  |  | E
13 |  | eTemp1_MSP_1A1_D | PID manual value from DCS | [6 empty] | 1 |  |  | 40025 | Write | REAL |  |  |  | O
14 |  | eTemp1_RESET_1A1_D | PID Reset from DCS | [6 empty] | 1 |  |  | 40027 | Write | REAL |  |  |  | E
15 |  | eTemp1_SP_1A1_D | PID setpoint from DCS | [6 empty] | 1 |  |  | 40029 | Write | REAL |  |  |  | O
16

## Register Table_Slave_DO
№ п/п | Функциональное обозначение по проекту Project Functional Designation | Tег ПЛК / Hаименование переменной PLC Tag/Variable Name | Описание переменной Description of the variable | Единицы измерения Units of measurement | Шкала scale | LL | LA | HA | HH | Коэффициенты масштабирования Scaling factors | Тип сигнала (Импульс/Постоянный ) Signal type (Impulse/Permanent) | Тип регистра Register type | Адрес/бит Address/Bit | Тип доступа Access type | Тип данных Data type | Код функции Function code | Канал РСУ DCS channel | Tег РСУ / Hаименование переменной DCS Tag/Name variable | Функции РСУ DCS functions | Примечание note
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
1 |  | h1130_PDT_34502_LL | Sealing gas differential pressure transmitter LL |  | 0-Alarm, 1-Normal | [6 empty] | 1 | 10001 | READ |  |  |  |  | A
2 |  | h1130_PT_34101_LL | Compressor suction line pressure LL |  | 0-Alarm, 1-Normal | [6 empty] | 2 | 10002 | READ |  |  |  |  | A
3 |  | h1130_PT_34102_LL | Compressor suction line pressure transmitter LL |  | 0-Alarm, 1-Normal | [6 empty] | 3 | 10003 | READ |  |  |  |  | A
4 |  | h1130_PT_34103_LL | Compressor suction line pressure transmitter LL |  | 0-Alarm, 1-Normal | [6 empty] | 4 | 10004 | READ |  |  |  |  | A
5 |  | h1130_PT_34104_LL | Compressor suction line pressure transmitter LL |  | 0-Alarm, 1-Normal | [6 empty] | 5 | 10005 | READ |  |  |  |  | A
6 |  | h1130_PT_34105_HH | Compressor discharge line pressure transmitter HH |  | 0-Alarm, 1-Normal | [6 empty] | 6 | 10006 | READ |  |  |  |  | A
7 |  | h1130_PT_34106_HH | Compressor discharge line pressure transmitter HH |  | 0-Alarm, 1-Normal | [6 empty] | 7 | 10007 | READ |  |  |  |  | A
8 |  | h1130_PT_34107_HH | Compressor discharge line pressure transmitter HH |  | 0-Alarm, 1-Normal | [6 empty] | 8 | 10008 | READ |  |  |  |  | A
9 |  | h1130_PT_34302_LL | Lubricating oil supply manifold pressure transmitter LL |  | 0-Alarm, 1-Normal | [6 empty] | 9 | 10009 | READ |  |  |  |  | A
10 |  | h1130_PT_34303_LL | Lubricating oil supply manifold pressure transmitter LL |  | 0-Alarm, 1-Normal | [6 empty] | 10 | 10010 | READ |  |  |  |  | A
11 |  | h1130_PT_34304_LL | Lubricating oil supply manifold pressure transmitter LL |  | 0-Alarm, 1-Normal | [6 empty] | 11 | 10011 | READ |  |  |  |  | A
12 |  | h1130_PT_35701_LL | Turbine exhaust pressure transmitter LL |  | 0-Alarm, 1-Normal | [6 empty] | 12 | 10012 | READ |  |  |  |  | A
13 |  | h1130_PT_35702_LL | Turbine exhaust pressure transmitter LL |  | 0-Alarm, 1-Normal | [6 empty] | 13 | 10013 | READ |  |  |  |  | A
14 |  | h1130_PT_35703_LL | Turbine exhaust pressure transmitter LL |  | 0-Alarm, 1-Normal | [6 empty] | 14 | 10014 | READ |  |  |  |  | A
15 |  | h1130_SE_35503_HH | Turbine speed sensor HH |  | 0-Alarm, 1-Normal | [6 empty] | 15 | 10015 | READ |  |  |  |  | A
16 |  | h1130_SE_35504_HH | Turbine speed sensor HH |  | 0-Alarm, 1-Normal | [6 empty] | 16 | 10016 | READ |  |  |  |  | A
17 |  | h1130_SE_35505_HH | Turbine speed sensor HH |  | 0-Alarm, 1-Normal | [6 empty] | 17 | 10017 | READ |  |  |  |  | A
18 |  | h1130_TE_34701_HH | Compressor suction male rotor radial bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 18 | 10018 | READ |  |  |  |  | A
19 |  | h1130_TE_34702_HH | Compressor suction male rotor radial bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 19 | 10019 | READ |  |  |  |  | A
20 |  | h1130_TE_34703_HH | Compressor suction female rotor radial bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 20 | 10020 | READ |  |  |  |  | A
21 |  | h1130_TE_34704_HH | Compressor suction female rotor radial bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 21 | 10021 | READ |  |  |  |  | A
22 |  | h1130_TE_34705_HH | Compressor discharge male rotor radial bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 22 | 10022 | READ |  |  |  |  | A
23 |  | h1130_TE_34706_HH | Compressor discharge male rotor radial bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 23 | 10023 | READ |  |  |  |  | A
24 |  | h1130_TE_34707_HH | Compressor discharge female rotor radial bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 24 | 10024 | READ |  |  |  |  | A
25 |  | h1130_TE_34708_HH | Compressor discharge female rotor radial bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 25 | 10025 | READ |  |  |  |  | A
26 |  | h1130_TE_34709_HH | Compressor male rotor thrust bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 26 | 10026 | READ |  |  |  |  | A
27 |  | h1130_TE_34710_HH | Compressor male rotor thrust bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 27 | 10027 | READ |  |  |  |  | A
28 |  | h1130_TE_34711_HH | Compressor female rotor thrust bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 28 | 10028 | READ |  |  |  |  | A
29 |  | h1130_TE_34712_HH | Compressor female rotor thrust bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 29 | 10029 | READ |  |  |  |  | A
30 |  | h1130_TE_34713_HH | Gear box bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 30 | 10030 | READ |  |  |  |  | A
31 |  | h1130_TE_34714_HH | Gear box bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 31 | 10031 | READ |  |  |  |  | A
32 |  | h1130_TE_34715_HH | Gear box bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 32 | 10032 | READ |  |  |  |  | A
33 |  | h1130_TE_34716_HH | Gear box bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 33 | 10033 | READ |  |  |  |  | A
34 |  | h1130_TE_34717_HH | Gear box bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 34 | 10034 | READ |  |  |  |  | A
35 |  | h1130_TE_34718_HH | Gear box bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 35 | 10035 | READ |  |  |  |  | A
36 |  | h1130_TE_34719_HH | Gear box bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 36 | 10036 | READ |  |  |  |  | A
37 |  | h1130_TE_34720_HH | Gear box bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 37 | 10037 | READ |  |  |  |  | A
38 |  | h1130_TE_34721_HH | Turbine bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 38 | 10038 | READ |  |  |  |  | A
39 |  | h1130_TE_34722_HH | Turbine bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 39 | 10039 | READ |  |  |  |  | A
40 |  | h1130_TE_34723_HH | Turbine bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 40 | 10040 | READ |  |  |  |  | A
41 |  | h1130_TE_34724_HH | Turbine bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 41 | 10041 | READ |  |  |  |  | A
42 |  | h1130_TE_34725_HH | Turbine thrust bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 42 | 10042 | READ |  |  |  |  | A
43 |  | h1130_TE_34726_HH | Turbine thrust bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 43 | 10043 | READ |  |  |  |  | A
44 |  | h1130_TE_34727_HH | Turbine thrust bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 44 | 10044 | READ |  |  |  |  | A
45 |  | h1130_TE_34728_HH | Turbine thrust bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 45 | 10045 | READ |  |  |  |  | A
46 |  | h1130_TT_34103_HH | Compressor discharge line temperature transmitter HH |  | 0-Alarm, 1-Normal | [6 empty] | 46 | 10046 | READ |  |  |  |  | A
47 |  | h1130_TT_34104_HH | Compressor discharge line temperature transmitter HH |  | 0-Alarm, 1-Normal | [6 empty] | 47 | 10047 | READ |  |  |  |  | A
48 |  | h1130_TT_34105_HH | Compressor discharge line temperature transmitter HH |  | 0-Alarm, 1-Normal | [6 empty] | 48 | 10048 | READ |  |  |  |  | A
49 |  | h1130_VE_34901_HH | Compressor bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 49 | 10049 | READ |  |  |  |  | A
50 |  | h1130_VE_34902_HH | Compressor bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 50 | 10050 | READ |  |  |  |  | A
51 |  | h1130_VE_34903_HH | Compressor bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 51 | 10051 | READ |  |  |  |  | A
52 |  | h1130_VE_34904_HH | Compressor bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 52 | 10052 | READ |  |  |  |  | A
53 |  | h1130_VE_34905_HH | Compressor bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 53 | 10053 | READ |  |  |  |  | A
54 |  | h1130_VE_34906_HH | Compressor bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 54 | 10054 | READ |  |  |  |  | A
55 |  | h1130_VE_34907_HH | Compressor bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 55 | 10055 | READ |  |  |  |  | A
56 |  | h1130_VE_34908_HH | Compressor bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 56 | 10056 | READ |  |  |  |  | A
57 |  | h1130_VE_34909_HH | Gear box bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 57 | 10057 | READ |  |  |  |  | A
58 |  | h1130_VE_34910_HH | Gear box bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 58 | 10058 | READ |  |  |  |  | A
59 |  | h1130_VE_34911_HH | Gear box bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 59 | 10059 | READ |  |  |  |  | A
60 |  | h1130_VE_34912_HH | Gear box bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 60 | 10060 | READ |  |  |  |  | A
61 |  | h1130_VE_34913_HH | Gear box bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 61 | 10061 | READ |  |  |  |  | A
62 |  | h1130_VE_34914_HH | Gear box bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 62 | 10062 | READ |  |  |  |  | A
63 |  | h1130_VE_34915_HH | Gear box bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 63 | 10063 | READ |  |  |  |  | A
64 |  | h1130_VE_34916_HH | Gear box bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 64 | 10064 | READ |  |  |  |  | A
65 |  | h1130_VE_34917_HH | Turbine bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 65 | 10065 | READ |  |  |  |  | A
66 |  | h1130_VE_34918_HH | Turbine bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 66 | 10066 | READ |  |  |  |  | A
67 |  | h1130_VE_34919_HH | Turbine bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 67 | 10067 | READ |  |  |  |  | A
68 |  | h1130_VE_34920_HH | Turbine bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 68 | 10068 | READ |  |  |  |  | A
69 |  | h1130_ZE_34901_HH | Compressor thrust bearing displacement HH |  | 0-Alarm, 1-Normal | [6 empty] | 69 | 10069 | READ |  |  |  |  | A
70 |  | h1130_ZE_34901_LL | Compressor thrust bearing displacement LL |  | 0-Alarm, 1-Normal | [6 empty] | 70 | 10070 | READ |  |  |  |  | A
71 |  | h1130_ZE_34902_HH | Compressor thrust bearing displacement HH |  | 0-Alarm, 1-Normal | [6 empty] | 71 | 10071 | READ |  |  |  |  | A
72 |  | h1130_ZE_34902_LL | Compressor thrust bearing displacement LL |  | 0-Alarm, 1-Normal | [6 empty] | 72 | 10072 | READ |  |  |  |  | A
73 |  | h1130_ZE_34903_HH | Compressor thrust bearing displacement HH |  | 0-Alarm, 1-Normal | [6 empty] | 73 | 10073 | READ |  |  |  |  | A
74 |  | h1130_ZE_34903_LL | Compressor thrust bearing displacement LL |  | 0-Alarm, 1-Normal | [6 empty] | 74 | 10074 | READ |  |  |  |  | A
75 |  | h1130_ZE_34904_HH | Compressor thrust bearing displacement HH |  | 0-Alarm, 1-Normal | [6 empty] | 75 | 10075 | READ |  |  |  |  | A
76 |  | h1130_ZE_34904_LL | Compressor thrust bearing displacement LL |  | 0-Alarm, 1-Normal | [6 empty] | 76 | 10076 | READ |  |  |  |  | A
77 |  | h1130_ZE_34905_HH | Turbine displacement HH |  | 0-Alarm, 1-Normal | [6 empty] | 77 | 10077 | READ |  |  |  |  | A
78 |  | h1130_ZE_34905_LL | Turbine displacement LL |  | 0-Alarm, 1-Normal | [6 empty] | 78 | 10078 | READ |  |  |  |  | A
79 |  | h1130_ZE_34906_HH | Turbine displacement HH |  | 0-Alarm, 1-Normal | [6 empty] | 79 | 10079 | READ |  |  |  |  | A
80 |  | h1130_ZE_34906_LL | Turbine displacement LL |  | 0-Alarm, 1-Normal | [6 empty] | 80 | 10080 | READ |  |  |  |  | A
81 |  | l1130_FT_34101_AF | Inlet fluid replenishment flow transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 81 | 10081 | READ |  |  |  |  | A
82 |  | l1130_FT_34501_AF | Sealing gas flow transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 82 | 10082 | READ |  |  |  |  | A
83 |  | l1130_FT_34501_L | Sealing gas flow transmitter L |  | 0-Alarm, 1-Normal | [6 empty] | 83 | 10083 | READ |  |  |  |  | A
84 |  | l1130_FT_34502_AF | Sealing gas flow transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 84 | 10084 | READ |  |  |  |  | A
85 |  | l1130_FT_34502_L | Sealing gas flow transmitter L |  | 0-Alarm, 1-Normal | [6 empty] | 85 | 10085 | READ |  |  |  |  | A
86 |  | l1130_FT_34503_AF | Sealing gas flow transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 86 | 10086 | READ |  |  |  |  | A
87 |  | l1130_FT_34503_L | Sealing gas flow transmitter L |  | 0-Alarm, 1-Normal | [6 empty] | 87 | 10087 | READ |  |  |  |  | A
88 |  | l1130_FT_34504_AF | Sealing gas flow transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 88 | 10088 | READ |  |  |  |  | A
89 |  | l1130_FT_34504_L | Sealing gas flow transmitter L |  | 0-Alarm, 1-Normal | [6 empty] | 89 | 10089 | READ |  |  |  |  | A
90 |  | l1130_LT_34301_AF | Lubricating oil tank level transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 90 | 10090 | READ |  |  |  |  | A
91 |  | l1130_LT_34301_L | Lubricating oil tank level transmitter L |  | 0-Alarm, 1-Normal | [6 empty] | 91 | 10091 | READ |  |  |  |  | A
92 |  | l1130_LT_34302_AF | Run down tank level transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 92 | 10092 | READ |  |  |  |  | A
93 |  | l1130_LT_34302_L | Run down tank level transmitter L |  | 0-Alarm, 1-Normal | [6 empty] | 93 | 10093 | READ |  |  |  |  | A
94 |  | l1130_PDT_34101_AF | Suction line filter differential pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 94 | 10094 | READ |  |  |  |  | A
95 |  | l1130_PDT_34101_H | Suction line filter differential pressure transmitter H |  | 0-Alarm, 1-Normal | [6 empty] | 95 | 10095 | READ |  |  |  |  | A
96 |  | l1130_PDT_34102_AF | Inlet fluid replenishment filter differential pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 96 | 10096 | READ |  |  |  |  | A
97 |  | l1130_PDT_34102_H | Inlet fluid replenishment filter differential pressure transmitter H |  | 0-Alarm, 1-Normal | [6 empty] | 97 | 10097 | READ |  |  |  |  | A
98 |  | l1130_PDT_34301_AF | Lubricating oil filter differential pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 98 | 10098 | READ |  |  |  |  | A
99 |  | l1130_PDT_34301_H | Lubricating oil filter differential pressure transmitter H |  | 0-Alarm, 1-Normal | [6 empty] | 99 | 10099 | READ |  |  |  |  | A
100 |  | l1130_PDT_34501_AF | Seal nitrogen inlet filter differential pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 100 | 10100 | READ |  |  |  |  | A
101 |  | l1130_PDT_34501_H | Seal nitrogen inlet filter differential pressure transmitter H |  | 0-Alarm, 1-Normal | [6 empty] | 101 | 10101 | READ |  |  |  |  | A
102 |  | l1130_PDT_34502_AF | Sealing gas differential pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 102 | 10102 | READ |  |  |  |  | A
103 |  | l1130_PDT_34502_L | Sealing gas differential pressure transmitter L |  | 0-Alarm, 1-Normal | [6 empty] | 103 | 10103 | READ |  |  |  |  | A
104 |  | l1130_PT_34101_AF | Compressor suction line pressure fault |  | 0-Alarm, 1-Normal | [6 empty] | 104 | 10104 | READ |  |  |  |  | A
105 |  | l1130_PT_34101_L | Compressor suction line pressure L |  | 0-Alarm, 1-Normal | [6 empty] | 105 | 10105 | READ |  |  |  |  | A
106 |  | l1130_PT_34102_AF | Compressor suction line pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 106 | 10106 | READ |  |  |  |  | A
107 |  | l1130_PT_34103_AF | Compressor suction line pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 107 | 10107 | READ |  |  |  |  | A
108 |  | l1130_PT_34104_AF | Compressor suction line pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 108 | 10108 | READ |  |  |  |  | A
109 |  | l1130_PT_34104_L | Compressor suction line pressure transmitter L |  | 0-Alarm, 1-Normal | [6 empty] | 109 | 10109 | READ |  |  |  |  | A
110 |  | l1130_PT_34105_AF | Compressor discharge line pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 110 | 10110 | READ |  |  |  |  | A
111 |  | l1130_PT_34105_H | Compressor discharge line pressure transmitter H |  | 0-Alarm, 1-Normal | [6 empty] | 111 | 10111 | READ |  |  |  |  | A
112 |  | l1130_PT_34106_AF | Compressor discharge line pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 112 | 10112 | READ |  |  |  |  | A
113 |  | l1130_PT_34106_H | Compressor discharge line pressure transmitter H |  | 0-Alarm, 1-Normal | [6 empty] | 113 | 10113 | READ |  |  |  |  | A
114 |  | l1130_PT_34107_AF | Compressor discharge line pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 114 | 10114 | READ |  |  |  |  | A
115 |  | l1130_PT_34107_H | Compressor discharge line pressure transmitter H |  | 0-Alarm, 1-Normal | [6 empty] | 115 | 10115 | READ |  |  |  |  | A
116 |  | l1130_PT_34301_AF | Pressure transmitter after lubricating oil filter fault |  | 0-Alarm, 1-Normal | [6 empty] | 116 | 10116 | READ |  |  |  |  | A
117 |  | l1130_PT_34301_L | Pressure transmitter after lubricating oil filter L |  | 0-Alarm, 1-Normal | [6 empty] | 117 | 10117 | READ |  |  |  |  | A
118 |  | l1130_PT_34302_AF | Lubricating oil supply manifold pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 118 | 10118 | READ |  |  |  |  | A
119 |  | l1130_PT_34303_AF | Lubricating oil supply manifold pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 119 | 10119 | READ |  |  |  |  | A
120 |  | l1130_PT_34304_AF | Lubricating oil supply manifold pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 120 | 10120 | READ |  |  |  |  | A
121 |  | l1130_PT_34501_AF | Sealing gas pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 121 | 10121 | READ |  |  |  |  | A
122 |  | l1130_PT_34501_L | Sealing gas pressure transmitter L |  | 0-Alarm, 1-Normal | [6 empty] | 122 | 10122 | READ |  |  |  |  | A
123 |  | l1130_PT_35301_AF | Turbine regulating oil pressure fault |  | 0-Alarm, 1-Normal | [6 empty] | 123 | 10123 | READ |  |  |  |  | A
124 |  | l1130_PT_35301_L | Turbine regulating oil pressure L |  | 0-Alarm, 1-Normal | [6 empty] | 124 | 10124 | READ |  |  |  |  | A
125 |  | l1130_PT_35501_AF | Turbine closing oil pressure fault |  | 0-Alarm, 1-Normal | [6 empty] | 125 | 10125 | READ |  |  |  |  | A
126 |  | l1130_PT_35501_L | Turbine closing oil pressure L |  | 0-Alarm, 1-Normal | [6 empty] | 126 | 10126 | READ |  |  |  |  | A
127 |  | l1130_PT_35701_AF | Turbine exhaust pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 127 | 10127 | READ |  |  |  |  | A
128 |  | l1130_PT_35701_H | Turbine exhaust pressure transmitter H |  | 0-Alarm, 1-Normal | [6 empty] | 128 | 10128 | READ |  |  |  |  | A
129 |  | l1130_PT_35701_L | Turbine exhaust pressure transmitter L |  | 0-Alarm, 1-Normal | [6 empty] | 129 | 10129 | READ |  |  |  |  | A
130 |  | l1130_PT_35702_AF | Turbine exhaust pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 130 | 10130 | READ |  |  |  |  | A
131 |  | l1130_PT_35702_H | Turbine exhaust pressure transmitter H |  | 0-Alarm, 1-Normal | [6 empty] | 131 | 10131 | READ |  |  |  |  | A
132 |  | l1130_PT_35702_L | Turbine exhaust pressure transmitter L |  | 0-Alarm, 1-Normal | [6 empty] | 132 | 10132 | READ |  |  |  |  | A
133 |  | l1130_PT_35703_AF | Turbine exhaust pressure transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 133 | 10133 | READ |  |  |  |  | A
134 |  | l1130_PT_35703_H | Turbine exhaust pressure transmitter H |  | 0-Alarm, 1-Normal | [6 empty] | 134 | 10134 | READ |  |  |  |  | A
135 |  | l1130_PT_35703_L | Turbine exhaust pressure transmitter L |  | 0-Alarm, 1-Normal | [6 empty] | 135 | 10135 | READ |  |  |  |  | A
136 |  | l1130_TE_34701_AF | Compressor suction male rotor radial bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 136 | 10136 | READ |  |  |  |  | A
137 |  | l1130_TE_34701_H | Compressor suction male rotor radial bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 137 | 10137 | READ |  |  |  |  | A
138 |  | l1130_TE_34702_AF | Compressor suction male rotor radial bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 138 | 10138 | READ |  |  |  |  | A
139 |  | l1130_TE_34702_H | Compressor suction male rotor radial bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 139 | 10139 | READ |  |  |  |  | A
140 |  | l1130_TE_34703_AF | Compressor suction female rotor radial bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 140 | 10140 | READ |  |  |  |  | A
141 |  | l1130_TE_34703_H | Compressor suction female rotor radial bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 141 | 10141 | READ |  |  |  |  | A
142 |  | l1130_TE_34704_AF | Compressor suction female rotor radial bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 142 | 10142 | READ |  |  |  |  | A
143 |  | l1130_TE_34704_H | Compressor suction female rotor radial bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 143 | 10143 | READ |  |  |  |  | A
144 |  | l1130_TE_34705_AF | Compressor discharge male rotor radial bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 144 | 10144 | READ |  |  |  |  | A
145 |  | l1130_TE_34705_H | Compressor discharge male rotor radial bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 145 | 10145 | READ |  |  |  |  | A
146 |  | l1130_TE_34706_AF | Compressor discharge male rotor radial bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 146 | 10146 | READ |  |  |  |  | A
147 |  | l1130_TE_34706_H | Compressor discharge male rotor radial bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 147 | 10147 | READ |  |  |  |  | A
148 |  | l1130_TE_34707_AF | Compressor discharge female rotor radial bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 148 | 10148 | READ |  |  |  |  | A
149 |  | l1130_TE_34707_H | Compressor discharge female rotor radial bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 149 | 10149 | READ |  |  |  |  | A
150 |  | l1130_TE_34708_AF | Compressor discharge female rotor radial bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 150 | 10150 | READ |  |  |  |  | A
151 |  | l1130_TE_34708_H | Compressor discharge female rotor radial bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 151 | 10151 | READ |  |  |  |  | A
152 |  | l1130_TE_34709_AF | Compressor male rotor thrust bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 152 | 10152 | READ |  |  |  |  | A
153 |  | l1130_TE_34709_H | Compressor male rotor thrust bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 153 | 10153 | READ |  |  |  |  | A
154 |  | l1130_TE_34710_AF | Compressor male rotor thrust bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 154 | 10154 | READ |  |  |  |  | A
155 |  | l1130_TE_34710_H | Compressor male rotor thrust bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 155 | 10155 | READ |  |  |  |  | A
156 |  | l1130_TE_34711_AF | Compressor female rotor thrust bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 156 | 10156 | READ |  |  |  |  | A
157 |  | l1130_TE_34711_H | Compressor female rotor thrust bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 157 | 10157 | READ |  |  |  |  | A
158 |  | l1130_TE_34712_AF | Compressor female rotor thrust bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 158 | 10158 | READ |  |  |  |  | A
159 |  | l1130_TE_34712_H | Compressor female rotor thrust bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 159 | 10159 | READ |  |  |  |  | A
160 |  | l1130_TE_34713_AF | Gear box bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 160 | 10160 | READ |  |  |  |  | A
161 |  | l1130_TE_34713_H | Gear box bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 161 | 10161 | READ |  |  |  |  | A
162 |  | l1130_TE_34714_AF | Gear box bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 162 | 10162 | READ |  |  |  |  | A
163 |  | l1130_TE_34714_H | Gear box bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 163 | 10163 | READ |  |  |  |  | A
164 |  | l1130_TE_34715_AF | Gear box bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 164 | 10164 | READ |  |  |  |  | A
165 |  | l1130_TE_34715_H | Gear box bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 165 | 10165 | READ |  |  |  |  | A
166 |  | l1130_TE_34716_AF | Gear box bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 166 | 10166 | READ |  |  |  |  | A
167 |  | l1130_TE_34716_H | Gear box bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 167 | 10167 | READ |  |  |  |  | A
168 |  | l1130_TE_34717_AF | Gear box bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 168 | 10168 | READ |  |  |  |  | A
169 |  | l1130_TE_34717_H | Gear box bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 169 | 10169 | READ |  |  |  |  | A
170 |  | l1130_TE_34718_AF | Gear box bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 170 | 10170 | READ |  |  |  |  | A
171 |  | l1130_TE_34718_H | Gear box bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 171 | 10171 | READ |  |  |  |  | A
172 |  | l1130_TE_34719_AF | Gear box bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 172 | 10172 | READ |  |  |  |  | A
173 |  | l1130_TE_34719_H | Gear box bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 173 | 10173 | READ |  |  |  |  | A
174 |  | l1130_TE_34720_AF | Gear box bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 174 | 10174 | READ |  |  |  |  | A
175 |  | l1130_TE_34720_H | Gear box bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 175 | 10175 | READ |  |  |  |  | A
176 |  | l1130_TE_34721_AF | Turbine bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 176 | 10176 | READ |  |  |  |  | A
177 |  | l1130_TE_34721_H | Turbine bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 177 | 10177 | READ |  |  |  |  | A
178 |  | l1130_TE_34722_AF | Turbine bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 178 | 10178 | READ |  |  |  |  | A
179 |  | l1130_TE_34722_H | Turbine bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 179 | 10179 | READ |  |  |  |  | A
180 |  | l1130_TE_34723_AF | Turbine bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 180 | 10180 | READ |  |  |  |  | A
181 |  | l1130_TE_34723_H | Turbine bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 181 | 10181 | READ |  |  |  |  | A
182 |  | l1130_TE_34724_AF | Turbine bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 182 | 10182 | READ |  |  |  |  | A
183 |  | l1130_TE_34724_H | Turbine bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 183 | 10183 | READ |  |  |  |  | A
184 |  | l1130_TE_34725_AF | Turbine thrust bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 184 | 10184 | READ |  |  |  |  | A
185 |  | l1130_TE_34725_H | Turbine thrust bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 185 | 10185 | READ |  |  |  |  | A
186 |  | l1130_TE_34726_AF | Turbine thrust bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 186 | 10186 | READ |  |  |  |  | A
187 |  | l1130_TE_34726_H | Turbine thrust bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 187 | 10187 | READ |  |  |  |  | A
188 |  | l1130_TE_34727_AF | Turbine thrust bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 188 | 10188 | READ |  |  |  |  | A
189 |  | l1130_TE_34727_H | Turbine thrust bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 189 | 10189 | READ |  |  |  |  | A
190 |  | l1130_TE_34728_AF | Turbine thrust bearing temperature fault |  | 0-Alarm, 1-Normal | [6 empty] | 190 | 10190 | READ |  |  |  |  | A
191 |  | l1130_TE_34728_H | Turbine thrust bearing temperature H |  | 0-Alarm, 1-Normal | [6 empty] | 191 | 10191 | READ |  |  |  |  | A
192 |  | l1130_TT_34101_AF | Compressor suction line temperature transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 192 | 10192 | READ |  |  |  |  | A
193 |  | l1130_TT_34101_H | Compressor suction line temperature transmitter H |  | 0-Alarm, 1-Normal | [6 empty] | 193 | 10193 | READ |  |  |  |  | A
194 |  | l1130_TT_34102_AF | Compressor discharge line temperature transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 194 | 10194 | READ |  |  |  |  | A
195 |  | l1130_TT_34102_H | Compressor discharge line temperature transmitter H |  | 0-Alarm, 1-Normal | [6 empty] | 195 | 10195 | READ |  |  |  |  | A
196 |  | l1130_TT_34103_AF | Compressor discharge line temperature transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 196 | 10196 | READ |  |  |  |  | A
197 |  | l1130_TT_34104_AF | Compressor discharge line temperature transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 197 | 10197 | READ |  |  |  |  | A
198 |  | l1130_TT_34105_AF | Compressor discharge line temperature transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 198 | 10198 | READ |  |  |  |  | A
199 |  | l1130_TT_34301_AF | Lubricating oil tank temperature transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 199 | 10199 | READ |  |  |  |  | A
200 |  | l1130_TT_34301_L | Lubricating oil tank temperature transmitter L |  | 0-Alarm, 1-Normal | [6 empty] | 200 | 10200 | READ |  |  |  |  | A
201 |  | l1130_TT_34302_AF | Lubricating oil supply manifold temperature transmitter fault |  | 0-Alarm, 1-Normal | [6 empty] | 201 | 10201 | READ |  |  |  |  | A
202 |  | l1130_TT_34302_H | Lubricating oil supply manifold temperature transmitter H |  | 0-Alarm, 1-Normal | [6 empty] | 202 | 10202 | READ |  |  |  |  | A
203 |  | l1130_TT_34302_L | Lubricating oil supply manifold temperature transmitter L |  | 0-Alarm, 1-Normal | [6 empty] | 203 | 10203 | READ |  |  |  |  | A
204 |  | l1130_TZT_34101_AF | Inlet fluid replenishing valve position feedback fault |  | 0-Alarm, 1-Normal | [6 empty] | 204 | 10204 | READ |  |  |  |  | A
205 |  | l1130_VE_34901_AF | Compressor bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 205 | 10205 | READ |  |  |  |  | A
206 |  | l1130_VE_34901_H | Compressor bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 206 | 10206 | READ |  |  |  |  | A
207 |  | l1130_VE_34902_AF | Compressor bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 207 | 10207 | READ |  |  |  |  | A
208 |  | l1130_VE_34902_H | Compressor bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 208 | 10208 | READ |  |  |  |  | A
209 |  | l1130_VE_34903_AF | Compressor bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 209 | 10209 | READ |  |  |  |  | A
210 |  | l1130_VE_34903_H | Compressor bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 210 | 10210 | READ |  |  |  |  | A
211 |  | l1130_VE_34904_AF | Compressor bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 211 | 10211 | READ |  |  |  |  | A
212 |  | l1130_VE_34904_H | Compressor bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 212 | 10212 | READ |  |  |  |  | A
213 |  | l1130_VE_34905_AF | Compressor bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 213 | 10213 | READ |  |  |  |  | A
214 |  | l1130_VE_34905_H | Compressor bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 214 | 10214 | READ |  |  |  |  | A
215 |  | l1130_VE_34906_AF | Compressor bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 215 | 10215 | READ |  |  |  |  | A
216 |  | l1130_VE_34906_H | Compressor bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 216 | 10216 | READ |  |  |  |  | A
217 |  | l1130_VE_34907_AF | Compressor bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 217 | 10217 | READ |  |  |  |  | A
218 |  | l1130_VE_34907_H | Compressor bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 218 | 10218 | READ |  |  |  |  | A
219 |  | l1130_VE_34908_AF | Compressor bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 219 | 10219 | READ |  |  |  |  | A
220 |  | l1130_VE_34908_H | Compressor bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 220 | 10220 | READ |  |  |  |  | A
221 |  | l1130_VE_34909_AF | Gear box bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 221 | 10221 | READ |  |  |  |  | A
222 |  | l1130_VE_34909_H | Gear box bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 222 | 10222 | READ |  |  |  |  | A
223 |  | l1130_VE_34910_AF | Gear box bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 223 | 10223 | READ |  |  |  |  | A
224 |  | l1130_VE_34910_H | Gear box bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 224 | 10224 | READ |  |  |  |  | A
225 |  | l1130_VE_34911_AF | Gear box bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 225 | 10225 | READ |  |  |  |  | A
226 |  | l1130_VE_34911_H | Gear box bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 226 | 10226 | READ |  |  |  |  | A
227 |  | l1130_VE_34912_AF | Gear box bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 227 | 10227 | READ |  |  |  |  | A
228 |  | l1130_VE_34912_H | Gear box bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 228 | 10228 | READ |  |  |  |  | A
229 |  | l1130_VE_34913_AF | Gear box bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 229 | 10229 | READ |  |  |  |  | A
230 |  | l1130_VE_34913_H | Gear box bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 230 | 10230 | READ |  |  |  |  | A
231 |  | l1130_VE_34914_AF | Gear box bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 231 | 10231 | READ |  |  |  |  | A
232 |  | l1130_VE_34914_H | Gear box bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 232 | 10232 | READ |  |  |  |  | A
233 |  | l1130_VE_34915_AF | Gear box bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 233 | 10233 | READ |  |  |  |  | A
234 |  | l1130_VE_34915_H | Gear box bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 234 | 10234 | READ |  |  |  |  | A
235 |  | l1130_VE_34916_AF | Gear box bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 235 | 10235 | READ |  |  |  |  | A
236 |  | l1130_VE_34916_H | Gear box bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 236 | 10236 | READ |  |  |  |  | A
237 |  | l1130_VE_34917_AF | Turbine bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 237 | 10237 | READ |  |  |  |  | A
238 |  | l1130_VE_34917_H | Turbine bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 238 | 10238 | READ |  |  |  |  | A
239 |  | l1130_VE_34918_AF | Turbine bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 239 | 10239 | READ |  |  |  |  | A
240 |  | l1130_VE_34918_H | Turbine bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 240 | 10240 | READ |  |  |  |  | A
241 |  | l1130_VE_34919_AF | Turbine bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 241 | 10241 | READ |  |  |  |  | A
242 |  | l1130_VE_34919_H | Turbine bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 242 | 10242 | READ |  |  |  |  | A
243 |  | l1130_VE_34920_AF | Turbine bearing vibration fault |  | 0-Alarm, 1-Normal | [6 empty] | 243 | 10243 | READ |  |  |  |  | A
244 |  | l1130_VE_34920_H | Turbine bearing vibration H |  | 0-Alarm, 1-Normal | [6 empty] | 244 | 10244 | READ |  |  |  |  | A
245 |  | l1130_ZE_34901_AF | Compressor thrust bearing displacement fault |  | 0-Alarm, 1-Normal | [6 empty] | 245 | 10245 | READ |  |  |  |  | A
246 |  | l1130_ZE_34901_H | Compressor thrust bearing displacement H |  | 0-Alarm, 1-Normal | [6 empty] | 246 | 10246 | READ |  |  |  |  | A
247 |  | l1130_ZE_34901_L | Compressor thrust bearing displacement L |  | 0-Alarm, 1-Normal | [6 empty] | 247 | 10247 | READ |  |  |  |  | A
248 |  | l1130_ZE_34902_AF | Compressor thrust bearing displacement fault |  | 0-Alarm, 1-Normal | [6 empty] | 248 | 10248 | READ |  |  |  |  | A
249 |  | l1130_ZE_34902_H | Compressor thrust bearing displacement H |  | 0-Alarm, 1-Normal | [6 empty] | 249 | 10249 | READ |  |  |  |  | A
250 |  | l1130_ZE_34902_L | Compressor thrust bearing displacement L |  | 0-Alarm, 1-Normal | [6 empty] | 250 | 10250 | READ |  |  |  |  | A
251 |  | l1130_ZE_34903_AF | Compressor thrust bearing displacement fault |  | 0-Alarm, 1-Normal | [6 empty] | 251 | 10251 | READ |  |  |  |  | A
252 |  | l1130_ZE_34903_H | Compressor thrust bearing displacement H |  | 0-Alarm, 1-Normal | [6 empty] | 252 | 10252 | READ |  |  |  |  | A
253 |  | l1130_ZE_34903_L | Compressor thrust bearing displacement L |  | 0-Alarm, 1-Normal | [6 empty] | 253 | 10253 | READ |  |  |  |  | A
254 |  | l1130_ZE_34904_AF | Compressor thrust bearing displacement fault |  | 0-Alarm, 1-Normal | [6 empty] | 254 | 10254 | READ |  |  |  |  | A
255 |  | l1130_ZE_34904_H | Compressor thrust bearing displacement H |  | 0-Alarm, 1-Normal | [6 empty] | 255 | 10255 | READ |  |  |  |  | A
256 |  | l1130_ZE_34904_L | Compressor thrust bearing displacement L |  | 0-Alarm, 1-Normal | [6 empty] | 256 | 10256 | READ |  |  |  |  | A
257 |  | l1130_ZE_34905_AF | Turbine displacement fault |  | 0-Alarm, 1-Normal | [6 empty] | 257 | 10257 | READ |  |  |  |  | A
258 |  | l1130_ZE_34905_H | Turbine displacement H |  | 0-Alarm, 1-Normal | [6 empty] | 258 | 10258 | READ |  |  |  |  | A
259 |  | l1130_ZE_34905_L | Turbine displacement L |  | 0-Alarm, 1-Normal | [6 empty] | 259 | 10259 | READ |  |  |  |  | A
260 |  | l1130_ZE_34906_AF | Turbine displacement fault |  | 0-Alarm, 1-Normal | [6 empty] | 260 | 10260 | READ |  |  |  |  | A
261 |  | l1130_ZE_34906_H | Turbine displacement H |  | 0-Alarm, 1-Normal | [6 empty] | 261 | 10261 | READ |  |  |  |  | A
262 |  | l1130_ZE_34906_L | Turbine displacement L |  | 0-Alarm, 1-Normal | [6 empty] | 262 | 10262 | READ |  |  |  |  | A
263 |  | c1130_LA_35901 | LCP ready to start light |  | 0-De-energized, 1-Energized | [6 empty] | 263 | 10263 | READ |  |  |  |  | A
264 |  | c1130_LA_35902 | LCP local control light |  | 0-De-energized, 1-Energized | [6 empty] | 264 | 10264 | READ |  |  |  |  | A
265 |  | c1130_TTV_35501 | Turbine solenoid valve |  | 0-Energized, 1-De-energized | [6 empty] | 265 | 10265 | READ |  |  |  |  | A
266 |  | c1130_TTV_35502 | Turbine solenoid valve |  | 0-Energized, 1-De-energized | [6 empty] | 266 | 10266 | READ |  |  |  |  | A
267 |  | c1130_XV_34101 | Relief valve(FO) |  | 0-Energized, 1-De-energized | [6 empty] | 267 | 10267 | READ |  |  |  |  | A
268 |  | c1130_YA_35901 | Interlock stop signal to SIS |  | 0-Alarm, 1-Normal | [6 empty] | 268 | 10268 | READ |  |  |  |  | A
269 |  | c1130_YA_35902 | ITCC interlock signal to ESD |  | 0-Alarm, 1-Normal | [6 empty] | 269 | 10269 | READ |  |  |  |  | A
270 |  | SPARE | [9 empty] | 270 | 10270 | READ |  |  |  |  | A
271 |  | c1130_MHS_35903 | Oil pump automatic enable start signal |  | 0-Normal, 1-Alarm | [6 empty] | 271 | 10271 | READ |  |  |  |  | A
272 |  | c1130_MHS_35904 | Oil pump automatic enable start signal |  | 0-Normal, 1-Alarm | [6 empty] | 272 | 10272 | READ |  |  |  |  | A
273 |  | c1130_MHS_35905 | Electric heater allows start signal |  | 0-Normal, 1-Alarm | [6 empty] | 273 | 10273 | READ |  |  |  |  | A
274 |  | c1130_MXA_35906 | ITCC running signal (Speed >500RPM) |  | 0-Normal, 1-Alarm | [6 empty] | 274 | 10274 | READ |  |  |  |  | A
275 |  | c1130_MHS_35901 | Oil pump A automatic start signal |  | 0-Normal, 1-Alarm | [6 empty] | 275 | 10275 | READ |  |  |  |  | A
276 |  | c1130_MHS_35902 | Oil pump B automatic start signal |  | 0-Normal, 1-Alarm | [6 empty] | 276 | 10276 | READ |  |  |  |  | A
277 |  | d1130_HZS_35902 | SIS emergency shutdown signal |  | 0-Alarm, 1-Normal | [6 empty] | 277 | 10277 | READ |  |  |  |  | A
278 |  | d1130_KST_301A_SB01 | LCP emergency stop button |  | 0-Alarm, 1-Normal | [6 empty] | 278 | 10278 | READ |  |  |  |  | A
279 |  | d1130_KST_301A_SB02 | LCP emergency stop button |  | 0-Alarm, 1-Normal | [6 empty] | 279 | 10279 | READ |  |  |  |  | A
280 |  | d1130_KST_301A_SB03 | LCP emergency stop button |  | 0-Alarm, 1-Normal | [6 empty] | 280 | 10280 | READ |  |  |  |  | A
281 |  | d1130_KST_301A_SB04 | LCP speed up button |  | 0-Alarm, 1-Normal | [6 empty] | 281 | 10281 | READ |  |  |  |  | A
282 |  | d1130_KST_301A_SB05 | LCP slow down button |  | 0-Alarm, 1-Normal | [6 empty] | 282 | 10282 | READ |  |  |  |  | A
283 |  | d1130_KST_301A_SB06 | LCP Overspeed test button |  | 0-Alarm, 1-Normal | [6 empty] | 283 | 10283 | READ |  |  |  |  | A
284 |  | d1130_XSC_34101 | Relief valve close position feedback |  | 0-Not Close, 1-Close | [6 empty] | 284 | 10284 | READ |  |  |  |  | A
285 |  | d1130_XSO_34101 | Relief valve open valve position feedback |  | 0-Not Open, 1-Open | [6 empty] | 285 | 10285 | READ |  |  |  |  | A
286 |  | d1130_MXA_35901 | Oil pump A running status |  | 0-Alarm, 1-Normal | [6 empty] | 286 | 10286 | READ |  |  |  |  | A
287 |  | d1130_MXA_35902 | Oil pump B running status |  | 0-Alarm, 1-Normal | [6 empty] | 287 | 10287 | READ |  |  |  |  | A
288 |  | d1130_MXA_35903 | Exhaust fan running status |  | 0-Alarm, 1-Normal | [6 empty] | 288 | 10288 | READ |  |  |  |  | A
289 |  | d1130_MXA_35904 | Turning motor running status |  | 0-Alarm, 1-Normal | [6 empty] | 289 | 10289 | READ |  |  |  |  | A
290 |  | d1130_MXA_35905 | Electric heater running status |  | 0-Alarm, 1-Normal | [6 empty] | 290 | 10290 | READ |  |  |  |  | A
291 |  | d1130_ZS_34901 | Turning gear position switch |  | 0-Normal, 1-Alarm | [6 empty] | 291 | 10291 | READ |  |  |  |  | A
292 |  | d1130_ZS_34902 | Turning gear position switch |  | 0-Normal, 1-Alarm | [6 empty] | 292 | 10292 | READ |  |  |  |  | A
293 |  | d1130_ZS_35501 | Turbine quick closing valve open position switch |  | 0-Not Open, 1-Open | [6 empty] | 293 | 10293 | READ |  |  |  |  | A
294 |  | d1130_ZS_35502 | Turbine quick closing valve close position switch |  | 0-Not Close, 1-Close | [6 empty] | 294 | 10294 | READ |  |  |  |  | A
295 |  | c1130_YA_35903 | ITCC interlock signal to DCS |  | 0-Alarm, 1-Normal | [6 empty] | 295 | 10295 | READ |  |  |  |  | A
296 |  | c1130_YL_35901 | ITCC alarm signal |  | 0-Alarm, 1-Normal | [6 empty] | 296 | 10296 | READ |  |  |  |  | A
297 |  | d1130_ITCC_AC_A | ITCC AC POWER ALARM |  | 0-Alarm, 1-Normal | [6 empty] | 297 | 10297 | READ |  |  |  |  | A
298 |  | d1130_ITCC_DOOR_A | ITCC DOOR LIMIT SWITCH ALARM |  | 0-Alarm, 1-Normal | [6 empty] | 298 | 10298 | READ |  |  |  |  | A
299 |  | d1130_ITCC_PSU_A | ITCC PSU ALARM |  | 0-Alarm, 1-Normal | [6 empty] | 299 | 10299 | READ |  |  |  |  | A
300 |  | d1130_ITCC_SYS_A | ITCC SYSTEM ALARM |  | 0-Alarm, 1-Normal | [6 empty] | 300 | 10300 | READ |  |  |  |  | A
301 |  | d1130_ITCC_TEM_A | ITCC TEMPERATURE ALARM |  | 0-Alarm, 1-Normal | [6 empty] | 301 | 10301 | READ |  |  |  |  | A
302 |  | d1130_MOS_ENABLE | Mos Enable signal from CCR |  | 0-Alarm, 1-Normal | [6 empty] | 302 | 10302 | READ |  |  |  |  | A
303 |  | f1130_FT_34501_BP | Sealing gas flow transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 303 | 10303 | READ |  |  |  |  | A
304 |  | f1130_FT_34502_BP | Sealing gas flow transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 304 | 10304 | READ |  |  |  |  | A
305 |  | f1130_FT_34503_BP | Sealing gas flow transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 305 | 10305 | READ |  |  |  |  | A
306 |  | f1130_FT_34504_BP | Sealing gas flow transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 306 | 10306 | READ |  |  |  |  | A
307 |  | f1130_HZS_35902 | SIS emergency stop button |  | 0-Alarm, 1-Normal | [6 empty] | 307 | 10307 | READ |  |  |  |  | A
308 |  | f1130_Heart_beat_1A1 | Heart beat signal |  | 0-Alarm, 1-Normal | [6 empty] | 308 | 10308 | READ |  |  |  |  | A
309 |  | f1130_ITCC_AC_A | ITCC AC POWER ALARM |  | 0-Alarm, 1-Normal | [6 empty] | 309 | 10309 | READ |  |  |  |  | A
310 |  | f1130_ITCC_DOOR_A | ITCC DOOR LIMIT SWITCH ALARM |  | 0-Alarm, 1-Normal | [6 empty] | 310 | 10310 | READ |  |  |  |  | A
311 |  | f1130_ITCC_PSU_A | ITCC PSU ALARM |  | 0-Alarm, 1-Normal | [6 empty] | 311 | 10311 | READ |  |  |  |  | A
312 |  | f1130_ITCC_SYS_A | ITCC SYSTEM ALARM |  | 0-Alarm, 1-Normal | [6 empty] | 312 | 10312 | READ |  |  |  |  | A
313 |  | f1130_ITCC_TEM_A | ITCC TEMPERATURE ALARM |  | 0-Alarm, 1-Normal | [6 empty] | 313 | 10313 | READ |  |  |  |  | A
314 |  | f1130_KST_301A_SB01 | LCP emergency stop button |  | 0-Alarm, 1-Normal | [6 empty] | 314 | 10314 | READ |  |  |  |  | A
315 |  | f1130_KST_301A_SB02 | LCP emergency stop button |  | 0-Alarm, 1-Normal | [6 empty] | 315 | 10315 | READ |  |  |  |  | A
316 |  | f1130_KST_301A_SB03 | LCP emergency stop button |  | 0-Alarm, 1-Normal | [6 empty] | 316 | 10316 | READ |  |  |  |  | A
317 |  | f1130_KST_301A_SB04 | LCP speed up button |  | 0-Normal, 1-Alarm | [6 empty] | 317 | 10317 | READ |  |  |  |  | A
318 |  | f1130_KST_301A_SB05 | LCP slow down button |  | 0-Normal, 1-Alarm | [6 empty] | 318 | 10318 | READ |  |  |  |  | A
319 |  | f1130_KST_301A_SB06 | LCP Overspeed test button |  | 0-Normal, 1-Alarm | [6 empty] | 319 | 10319 | READ |  |  |  |  | A
320 |  | f1130_LT_34301_BP | Lubricating oil tank level transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 320 | 10320 | READ |  |  |  |  | A
321 |  | f1130_LT_34302_BP | Run down tank level transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 321 | 10321 | READ |  |  |  |  | A
322 |  | f1130_MOS_Enable_1A1 | Mos enable button from CCR |  | 0-Normal, 1-Enabled | [6 empty] | 322 | 10322 | READ |  |  |  |  | A
323 |  | f1130_MXA_35901 | Oil pump A running status |  | 0-Alarm, 1-Normal | [6 empty] | 323 | 10323 | READ |  |  |  |  | A
324 |  | f1130_MXA_35902 | Oil pump B running status |  | 0-Alarm, 1-Normal | [6 empty] | 324 | 10324 | READ |  |  |  |  | A
325 |  | f1130_MXA_35903 | Exhaust fan running status |  | 0-Alarm, 1-Normal | [6 empty] | 325 | 10325 | READ |  |  |  |  | A
326 |  | f1130_MXA_35904 | Turning motor running status |  | 0-Alarm, 1-Normal | [6 empty] | 326 | 10326 | READ |  |  |  |  | A
327 |  | f1130_MXA_35905 | Electric heater running status |  | 0-Alarm, 1-Normal | [6 empty] | 327 | 10327 | READ |  |  |  |  | A
328 |  | f1130_PB_35901ABC | LCP emergency stop button |  | 0-Alarm, 1-Normal | [6 empty] | 328 | 10328 | READ |  |  |  |  | A
329 |  | f1130_PDT_34101_BP | Suction line filter differential pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 329 | 10329 | READ |  |  |  |  | A
330 |  | f1130_PDT_34102_BP | Inlet fluid replenishment filter differential pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 330 | 10330 | READ |  |  |  |  | A
331 |  | f1130_PDT_34301_BP | Lubricating oil filter differential pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 331 | 10331 | READ |  |  |  |  | A
332 |  | f1130_PDT_34501_BP | Seal nitrogen inlet filter differential pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 332 | 10332 | READ |  |  |  |  | A
333 |  | f1130_PDT_34502_BP | Sealing gas differential pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 333 | 10333 | READ |  |  |  |  | A
334 |  | f1130_PT_34101_BP | Compressor suction line pressure bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 334 | 10334 | READ |  |  |  |  | A
335 |  | f1130_PT_34102_BP | Compressor suction line pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 335 | 10335 | READ |  |  |  |  | A
336 |  | f1130_PT_34103_BP | Compressor suction line pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 336 | 10336 | READ |  |  |  |  | A
337 |  | f1130_PT_34104_BP | Compressor suction line pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 337 | 10337 | READ |  |  |  |  | A
338 |  | f1130_PT_34105_BP | Compressor discharge line pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 338 | 10338 | READ |  |  |  |  | A
339 |  | f1130_PT_34106_BP | Compressor discharge line pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 339 | 10339 | READ |  |  |  |  | A
340 |  | f1130_PT_34107_BP | Compressor discharge line pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 340 | 10340 | READ |  |  |  |  | A
341 |  | f1130_PT_34301_BP | Pressure transmitter after lubricating oil filter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 341 | 10341 | READ |  |  |  |  | A
342 |  | f1130_PT_34302_BP | Lubricating oil supply manifold pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 342 | 10342 | READ |  |  |  |  | A
343 |  | f1130_PT_34303_BP | Lubricating oil supply manifold pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 343 | 10343 | READ |  |  |  |  | A
344 |  | f1130_PT_34304_BP | Lubricating oil supply manifold pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 344 | 10344 | READ |  |  |  |  | A
345 |  | f1130_PT_34501_BP | Sealing gas pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 345 | 10345 | READ |  |  |  |  | A
346 |  | f1130_PT_35301_BP | Turbine regulating oil pressure bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 346 | 10346 | READ |  |  |  |  | A
347 |  | f1130_PT_35501_BP | Turbine closing oil pressure bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 347 | 10347 | READ |  |  |  |  | A
348 |  | f1130_PT_35701_BP | Turbine exhaust pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 348 | 10348 | READ |  |  |  |  | A
349 |  | f1130_PT_35702_BP | Turbine exhaust pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 349 | 10349 | READ |  |  |  |  | A
350 |  | f1130_PT_35703_BP | Turbine exhaust pressure transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 350 | 10350 | READ |  |  |  |  | A
351 |  | f1130_SE_35503_BP | Turbine speed sensor BP |  | 0-Normal, 1-Bypassed | [6 empty] | 351 | 10351 | READ |  |  |  |  | A
352 |  | f1130_SE_35504_BP | Turbine speed sensor BP |  | 0-Normal, 1-Bypassed | [6 empty] | 352 | 10352 | READ |  |  |  |  | A
353 |  | f1130_SE_35505_BP | Turbine speed sensor BP |  | 0-Normal, 1-Bypassed | [6 empty] | 353 | 10353 | READ |  |  |  |  | A
354 |  | f1130_TE_34701_BP | Compressor suction male rotor radial bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 354 | 10354 | READ |  |  |  |  | A
355 |  | f1130_TE_34702_BP | Compressor suction male rotor radial bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 355 | 10355 | READ |  |  |  |  | A
356 |  | f1130_TE_34703_BP | Compressor suction female rotor radial bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 356 | 10356 | READ |  |  |  |  | A
357 |  | f1130_TE_34704_BP | Compressor suction female rotor radial bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 357 | 10357 | READ |  |  |  |  | A
358 |  | f1130_TE_34705_BP | Compressor discharge male rotor radial bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 358 | 10358 | READ |  |  |  |  | A
359 |  | f1130_TE_34706_BP | Compressor discharge male rotor radial bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 359 | 10359 | READ |  |  |  |  | A
360 |  | f1130_TE_34707_BP | Compressor discharge female rotor radial bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 360 | 10360 | READ |  |  |  |  | A
361 |  | f1130_TE_34708_BP | Compressor discharge female rotor radial bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 361 | 10361 | READ |  |  |  |  | A
362 |  | f1130_TE_34709_BP | Compressor male rotor thrust bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 362 | 10362 | READ |  |  |  |  | A
363 |  | f1130_TE_34710_BP | Compressor male rotor thrust bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 363 | 10363 | READ |  |  |  |  | A
364 |  | f1130_TE_34711_BP | Compressor female rotor thrust bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 364 | 10364 | READ |  |  |  |  | A
365 |  | f1130_TE_34712_BP | Compressor female rotor thrust bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 365 | 10365 | READ |  |  |  |  | A
366 |  | f1130_TE_34713_BP | Gear box bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 366 | 10366 | READ |  |  |  |  | A
367 |  | f1130_TE_34714_BP | Gear box bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 367 | 10367 | READ |  |  |  |  | A
368 |  | f1130_TE_34715_BP | Gear box bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 368 | 10368 | READ |  |  |  |  | A
369 |  | f1130_TE_34716_BP | Gear box bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 369 | 10369 | READ |  |  |  |  | A
370 |  | f1130_TE_34717_BP | Gear box bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 370 | 10370 | READ |  |  |  |  | A
371 |  | f1130_TE_34718_BP | Gear box bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 371 | 10371 | READ |  |  |  |  | A
372 |  | f1130_TE_34719_BP | Gear box bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 372 | 10372 | READ |  |  |  |  | A
373 |  | f1130_TE_34720_BP | Gear box bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 373 | 10373 | READ |  |  |  |  | A
374 |  | f1130_TE_34721_BP | Turbine bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 374 | 10374 | READ |  |  |  |  | A
375 |  | f1130_TE_34722_BP | Turbine bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 375 | 10375 | READ |  |  |  |  | A
376 |  | f1130_TE_34723_BP | Turbine bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 376 | 10376 | READ |  |  |  |  | A
377 |  | f1130_TE_34724_BP | Turbine bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 377 | 10377 | READ |  |  |  |  | A
378 |  | f1130_TE_34725_BP | Turbine thrust bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 378 | 10378 | READ |  |  |  |  | A
379 |  | f1130_TE_34726_BP | Turbine thrust bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 379 | 10379 | READ |  |  |  |  | A
380 |  | f1130_TE_34727_BP | Turbine thrust bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 380 | 10380 | READ |  |  |  |  | A
381 |  | f1130_TE_34728_BP | Turbine thrust bearing temperature bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 381 | 10381 | READ |  |  |  |  | A
382 |  | f1130_TT_34101_BP | Compressor suction line temperature transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 382 | 10382 | READ |  |  |  |  | A
383 |  | f1130_TT_34102_BP | Compressor discharge line temperature transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 383 | 10383 | READ |  |  |  |  | A
384 |  | f1130_TT_34103_BP | Compressor discharge line temperature transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 384 | 10384 | READ |  |  |  |  | A
385 |  | f1130_TT_34104_BP | Compressor discharge line temperature transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 385 | 10385 | READ |  |  |  |  | A
386 |  | f1130_TT_34105_BP | Compressor discharge line temperature transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 386 | 10386 | READ |  |  |  |  | A
387 |  | f1130_TT_34301_BP | Lubricating oil tank temperature transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 387 | 10387 | READ |  |  |  |  | A
388 |  | f1130_TT_34302_BP | Lubricating oil supply manifold temperature transmitter bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 388 | 10388 | READ |  |  |  |  | A
389 |  | f1130_VE_34901_BP | Compressor bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 389 | 10389 | READ |  |  |  |  | A
390 |  | f1130_VE_34902_BP | Compressor bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 390 | 10390 | READ |  |  |  |  | A
391 |  | f1130_VE_34903_BP | Compressor bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 391 | 10391 | READ |  |  |  |  | A
392 |  | f1130_VE_34904_BP | Compressor bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 392 | 10392 | READ |  |  |  |  | A
393 |  | f1130_VE_34905_BP | Compressor bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 393 | 10393 | READ |  |  |  |  | A
394 |  | f1130_VE_34906_BP | Compressor bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 394 | 10394 | READ |  |  |  |  | A
395 |  | f1130_VE_34907_BP | Compressor bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 395 | 10395 | READ |  |  |  |  | A
396 |  | f1130_VE_34908_BP | Compressor bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 396 | 10396 | READ |  |  |  |  | A
397 |  | f1130_VE_34909_BP | Gear box bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 397 | 10397 | READ |  |  |  |  | A
398 |  | f1130_VE_34910_BP | Gear box bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 398 | 10398 | READ |  |  |  |  | A
399 |  | f1130_VE_34911_BP | Gear box bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 399 | 10399 | READ |  |  |  |  | A
400 |  | f1130_VE_34912_BP | Gear box bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 400 | 10400 | READ |  |  |  |  | A
401 |  | f1130_VE_34913_BP | Gear box bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 401 | 10401 | READ |  |  |  |  | A
402 |  | f1130_VE_34914_BP | Gear box bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 402 | 10402 | READ |  |  |  |  | A
403 |  | f1130_VE_34915_BP | Gear box bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 403 | 10403 | READ |  |  |  |  | A
404 |  | f1130_VE_34916_BP | Gear box bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 404 | 10404 | READ |  |  |  |  | A
405 |  | f1130_VE_34917_BP | Turbine bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 405 | 10405 | READ |  |  |  |  | A
406 |  | f1130_VE_34918_BP | Turbine bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 406 | 10406 | READ |  |  |  |  | A
407 |  | f1130_VE_34919_BP | Turbine bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 407 | 10407 | READ |  |  |  |  | A
408 |  | f1130_VE_34920_BP | Turbine bearing vibration bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 408 | 10408 | READ |  |  |  |  | A
409 |  | f1130_XSC_34101 | Relief valve close position feedback |  | 0-Normal, 1-Closed | [6 empty] | 409 | 10409 | READ |  |  |  |  | A
410 |  | f1130_XSO_34101 | Relief valve open valve position feedback |  | 0-Normal, 1-Open | [6 empty] | 410 | 10410 | READ |  |  |  |  | A
411 |  | f1130_YFO_35901 | Turbine start failure trip signal |  | 0-Alarm, 1-Normal | [6 empty] | 411 | 10411 | READ |  |  |  |  | A
412 |  | f1130_ZE_34901_BP | Compressor thrust bearing displacement bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 412 | 10412 | READ |  |  |  |  | A
413 |  | f1130_ZE_34902_BP | Compressor thrust bearing displacement bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 413 | 10413 | READ |  |  |  |  | A
414 |  | f1130_ZE_34903_BP | Compressor thrust bearing displacement bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 414 | 10414 | READ |  |  |  |  | A
415 |  | f1130_ZE_34904_BP | Compressor thrust bearing displacement bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 415 | 10415 | READ |  |  |  |  | A
416 |  | f1130_ZE_34905_BP | Turbine displacement bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 416 | 10416 | READ |  |  |  |  | A
417 |  | f1130_ZE_34906_BP | Turbine displacement bypass |  | 0-Normal, 1-Bypassed | [6 empty] | 417 | 10417 | READ |  |  |  |  | A
418 |  | f1130_ZS_34901 | Turning gear position switch |  | 0-Normal, 1-Alarm | [6 empty] | 418 | 10418 | READ |  |  |  |  | A
419 |  | f1130_ZS_34902 | Turning gear position switch |  | 0-Normal, 1-Alarm | [6 empty] | 419 | 10419 | READ |  |  |  |  | A
420 |  | f1130_ZS_35501 | Turbine quick closing valve open position switch |  | 0-Not Open, 1-Open | [6 empty] | 420 | 10420 | READ |  |  |  |  | A
421 |  | f1130_ZS_35502 | Turbine quick closing valve close position switch |  | 0-Not Close, 1-Close | [6 empty] | 421 | 10421 | READ |  |  |  |  | A
422 |  | fFlow1_AM_1A1 | PID manual auto |  | 0-Manual, 1-Auto | [6 empty] | 422 | 10422 | READ |  |  |  |  | A
423 |  | fHD2_1A1 | Governor- raise button |  | 0-Normal, 1-Alarm | [6 empty] | 423 | 10423 | READ |  |  |  |  | A
424 |  | fHD3_1A1 | Governor- lower button |  | 0-Normal, 1-Alarm | [6 empty] | 424 | 10424 | READ |  |  |  |  | A
425 |  | fLOWER_SPD_1A1 | Governor- lower button |  | 0-Normal, 1-Alarm | [6 empty] | 425 | 10425 | READ |  |  |  |  | A
426 |  | Spare | [9 empty] | 426 | 10426 | READ
427 |  | fLP1_ST_1A1 | 1# lubricating oil pump start |  | 0-Normal, 1-Start | [6 empty] | 427 | 10427 | READ |  |  |  |  | A
428 |  | fLP2_ST_1A1 | 2# lubricating oil pump start |  | 0-Normal, 1-Start | [6 empty] | 428 | 10428 | READ |  |  |  |  | A
429 |  | fLP_LOWPRESS_1A1 | lubricating oil pressure low |  | 0-Alarm, 1-Normal | [6 empty] | 429 | 10429 | READ |  |  |  |  | A
430 |  | fLP_PER_1A1 | Lubricating oil pump permit to start |  | 0-not permit, 1-Permit | [6 empty] | 430 | 10430 | READ |  |  |  |  | A
431 |  | fNORM_STP_1A1 | Governor- normal stop |  | 0-Alarm, 1-Normal | [6 empty] | 431 | 10431 | READ |  |  |  |  | A
432 |  | fRESET_TRIP_1A1 | Reset |  | 0-Normal, 1-Reset | [6 empty] | 432 | 10432 | READ |  |  |  |  | A
433 |  | fSA_1A1 | GOVERNOR-REMOTE/LOCAL SELECTOR |  | 0-Remote, 1-Local | [6 empty] | 433 | 10433 | READ |  |  |  |  | A
434 |  | fSTART_1A1 | Governor-Start |  | 0-Normal, 1-Start | [6 empty] | 434 | 10434 | READ |  |  |  |  | A
435 |  | fSTART_AM_1A1 | Governor- auto raise |  | 0-Manual, 1-Auto | [6 empty] | 435 | 10435 | READ |  |  |  |  | A
436 |  | fSTART_OK_1A1 | Start conditions are OK |  | 0-Not OK, 1-OK | [6 empty] | 436 | 10436 | READ |  |  |  |  | A
437 |  | fSTART_PERM_1A1 | Permit to start |  | 0-not permit, 1-Permit | [6 empty] | 437 | 10437 | READ |  |  |  |  | A
438 |  | fTemp1_AM_1A1 | PID manual auto |  | 0-Auto, 1-Manual | [6 empty] | 438 | 10438 | READ |  |  |  |  | A
439 |  | fTRIP_COMM_1A1 | Common Trip |  | 0-Alarm, 1-Normal | [6 empty] | 439 | 10439 | READ |  |  |  |  | A
440 |  | fWM1_C_H_1A1 | Governor-1= warm state 0= cold state |  | 0-cold state, 1-warm state | [6 empty] | 440 | 10440 | READ |  |  |  |  | A
441 |  | l1130_FT_34101_L | Inlet fluid replenishment flow transmitter L |  | 0-Alarm, 1-Normal | [6 empty] | 441 | 10441 | READ |  |  |  |  | A
442 |  | l1130_PT_30604_AF | Turbine speed governing inlet pressure drop to 7KPAG fault |  | 0-Alarm, 1-Normal | [6 empty] | 442 | 10442 | READ |  |  |  |  | A
443 |  | lPU1_F_1A1 | Governor-speed sensor 1 fault |  | 0-Alarm, 1-Normal | [6 empty] | 443 | 10443 | READ |  |  |  |  | A
444 |  | lPU2_F_1A1 | Governor-speed sensor 2 fault |  | 0-Alarm, 1-Normal | [6 empty] | 444 | 10444 | READ |  |  |  |  | A
445 |  | t1130_PT_3410123_LL | Compressor suction line pressure transmitter LL |  | 0-Alarm, 1-Normal | [6 empty] | 445 | 10445 | READ |  |  |  |  | A
446 |  | t1130_PT_3430234_LL | Lubricating oil supply manifold pressure transmitter LL |  | 0-Alarm, 1-Normal | [6 empty] | 446 | 10446 | READ |  |  |  |  | A
447 |  | t1130_PT_3570123_LL | Turbine exhaust pressure transmitter LL |  | 0-Alarm, 1-Normal | [6 empty] | 447 | 10447 | READ |  |  |  |  | A
448 |  | t1130_SE_3550345_HH | Turbine speed sensor HH |  | 0-Alarm, 1-Normal | [6 empty] | 448 | 10448 | READ |  |  |  |  | A
449 |  | t1130_TE_3470910_HH | Compressor male rotor thrust bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 449 | 10449 | READ |  |  |  |  | A
450 |  | t1130_TE_3471920_HH | Gear box bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 450 | 10450 | READ |  |  |  |  | A
451 |  | t1130_TT_3410345_HH | Compressor discharge line temperature transmitter HH |  | 0-Alarm, 1-Normal | [6 empty] | 451 | 10451 | READ |  |  |  |  | A
452 |  | t1130_VE_3491920_HH | Turbine bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 452 | 10452 | READ |  |  |  |  | A
453 |  | t1130_VE_349012_HH | Compressor bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 453 | 10453 | READ |  |  |  |  | A
454 |  | t1130_VE_349034_HH | Compressor bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 454 | 10454 | READ |  |  |  |  | A
455 |  | t1130_VE_349056_HH | Compressor bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 455 | 10455 | READ |  |  |  |  | A
456 |  | t1130_VE_349078_HH | Compressor bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 456 | 10456 | READ |  |  |  |  | A
457 |  | t1130_VE_349101_HH | Gear box bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 457 | 10457 | READ |  |  |  |  | A
458 |  | t1130_VE_349112_HH | Gear box bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 458 | 10458 | READ |  |  |  |  | A
459 |  | t1130_VE_349134_HH | Gear box bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 459 | 10459 | READ |  |  |  |  | A
460 |  | t1130_VE_349156_HH | Gear box bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 460 | 10460 | READ |  |  |  |  | A
461 |  | t1130_VE_349178_HH | Turbine bearing vibration HH |  | 0-Alarm, 1-Normal | [6 empty] | 461 | 10461 | READ |  |  |  |  | A
462 |  | t1130_ZE_349012_HH | Compressor thrust bearing displacement HH |  | 0-Alarm, 1-Normal | [6 empty] | 462 | 10462 | READ |  |  |  |  | A
463 |  | t1130_ZE_349034_HH | Compressor thrust bearing displacement HH |  | 0-Alarm, 1-Normal | [6 empty] | 463 | 10463 | READ |  |  |  |  | A
464 |  | t1130_ZE_349056_HH | Turbine displacement HH |  | 0-Alarm, 1-Normal | [6 empty] | 464 | 10464 | READ |  |  |  |  | A
465 |  | t1130_TE_347012_HH | Compressor suction male rotor radial bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 465 | 10465 | READ |  |  |  |  | A
466 |  | t1130_TE_347045_HH | Compressor suction female rotor radial bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 466 | 10466 | READ |  |  |  |  | A
467 |  | t1130_TE_347056_HH | Compressor discharge male rotor radial bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 467 | 10467 | READ |  |  |  |  | A
468 |  | t1130_TE_347078_HH | Compressor discharge female rotor radial bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 468 | 10468 | READ |  |  |  |  | A
469 |  | t1130_TE_347112_HH | Compressor female rotor thrust bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 469 | 10469 | READ |  |  |  |  | A
470 |  | t1130_TE_347134_HH | Gear box bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 470 | 10470 | READ |  |  |  |  | A
471 |  | t1130_TE_347156_HH | Gear box bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 471 | 10471 | READ |  |  |  |  | A
472 |  | t1130_TE_347178_HH | Gear box bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 472 | 10472 | READ |  |  |  |  | A
473 |  | t1130_TE_347212_HH | Turbine bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 473 | 10473 | READ |  |  |  |  | A
474 |  | t1130_TE_347234_HH | Turbine bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 474 | 10474 | READ |  |  |  |  | A
475 |  | t1130_TE_347256_HH | Turbine thrust bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 475 | 10475 | READ |  |  |  |  | A
476 |  | t1130_TE_347278_HH | Turbine thrust bearing temperature HH |  | 0-Alarm, 1-Normal | [6 empty] | 476 | 10476 | READ |  |  |  |  | A
477 |  | t1130_PT_3410567_HH | Compressor discharge line pressure transmitter HH |  | 0-Alarm, 1-Normal | [6 empty] | 477 | 10477 | READ |  |  |  |  | A
478 |  | fCommissioning_Mode_1A1 | Commissioning Mode |  | 0-Normal, 1-Commissioning mode | [6 empty] | 478 | 10478 | READ |  |  |  |  | A
479 |  | fDCS_HMI_1A1 | HMI_DCS control switch |  | 0-DCS Control, 1-HMI Control | [6 empty] | 479 | 10479 | READ |  |  |  |  | A

## Register Table_Slave_DI
№ п/п | Функциональное обозначение по проекту Project Functional Designation | Tег ПЛК / Hаименование переменной PLC Tag/Variable Name | Описание переменной Description of the variable | Единицы измерения Units of measurement | Шкала scale | LL | LA | HA | HH | Коэффициенты масштабирования Scaling factors | Тип сигнала (Импульс/Постоянный ) Signal type (Impulse/Permanent) | Тип регистра Register type | Адрес/бит Address/Bit | Тип доступа Access type | Тип данных Data type | Код функции Function code | Канал РСУ DCS channel | Tег РСУ / Hаименование переменной DCS Tag/Name variable | Функции РСУ DCS functions | Примечание note
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
1 |  | g1130_FT_34501_BP_D | Sealing gas flow transmitter bypass from DCS | [7 empty] | D | 0 | 1 | Write |  |  |  |  | E
2 |  | g1130_FT_34502_BP_D | Sealing gas flow transmitter bypass from DCS | [7 empty] | D | 0 | 2 | Write |  |  |  |  | E
3 |  | g1130_FT_34503_BP_D | Sealing gas flow transmitter bypass from DCS | [7 empty] | D | 0 | 3 | Write |  |  |  |  | E
4 |  | g1130_FT_34504_BP_D | Sealing gas flow transmitter bypass from DCS | [7 empty] | D | 0 | 4 | Write |  |  |  |  | E
5 |  | g1130_LT_34301_BP_D | Lubricating oil tank level transmitter bypass from DCS | [7 empty] | D | 0 | 5 | Write |  |  |  |  | E
6 |  | g1130_LT_34302_BP_D | Run down tank level transmitter bypass from DCS | [7 empty] | D | 0 | 6 | Write |  |  |  |  | E
7 |  | g1130_PDT_34101_BP_D | Suction line filter differential pressure transmitter bypass from DCS | [7 empty] | D | 0 | 7 | Write |  |  |  |  | E
8 |  | g1130_PDT_34102_BP_D | Inlet fluid replenishment filter differential pressure transmitter bypass from DCS | [7 empty] | D | 0 | 8 | Write |  |  |  |  | E
9 |  | g1130_PDT_34301_BP_D | Lubricating oil filter differential pressure transmitter bypass from DCS | [7 empty] | D | 0 | 9 | Write |  |  |  |  | E
10 |  | g1130_PDT_34501_BP_D | Seal nitrogen inlet filter differential pressure transmitter bypass from DCS | [7 empty] | D | 0 | 10 | Write |  |  |  |  | E
11 |  | g1130_PDT_34502_BP_D | Sealing gas differential pressure transmitter bypass from DCS | [7 empty] | D | 0 | 11 | Write |  |  |  |  | E
12 |  | g1130_PT_34101_BP_D | Compressor suction line pressure bypass from DCS | [7 empty] | D | 0 | 12 | Write |  |  |  |  | E
13 |  | g1130_PT_34102_BP_D | Compressor suction line pressure transmitter bypass from DCS | [7 empty] | D | 0 | 13 | Write |  |  |  |  | E
14 |  | g1130_PT_34103_BP_D | Compressor suction line pressure transmitter bypass from DCS | [7 empty] | D | 0 | 14 | Write |  |  |  |  | E
15 |  | g1130_PT_34104_BP_D | Compressor suction line pressure transmitter bypass from DCS | [7 empty] | D | 0 | 15 | Write |  |  |  |  | E
16 |  | g1130_PT_34105_BP_D | Compressor discharge line pressure transmitter bypass from DCS | [7 empty] | D | 0 | 16 | Write |  |  |  |  | E
17 |  | g1130_PT_34106_BP_D | Compressor discharge line pressure transmitter bypass from DCS | [7 empty] | D | 0 | 17 | Write |  |  |  |  | E
18 |  | g1130_PT_34107_BP_D | Compressor discharge line pressure transmitter bypass from DCS | [7 empty] | D | 0 | 18 | Write |  |  |  |  | E
19 |  | g1130_PT_34301_BP_D | Pressure transmitter after lubricating oil filter bypass from DCS | [7 empty] | D | 0 | 19 | Write |  |  |  |  | E
20 |  | g1130_PT_34302_BP_D | Lubricating oil supply manifold pressure transmitter bypass from DCS | [7 empty] | D | 0 | 20 | Write |  |  |  |  | E
21 |  | g1130_PT_34303_BP_D | Lubricating oil supply manifold pressure transmitter bypass from DCS | [7 empty] | D | 0 | 21 | Write |  |  |  |  | E
22 |  | g1130_PT_34304_BP_D | Lubricating oil supply manifold pressure transmitter bypass from DCS | [7 empty] | D | 0 | 22 | Write |  |  |  |  | E
23 |  | g1130_PT_34501_BP_D | Sealing gas pressure transmitter bypass from DCS | [7 empty] | D | 0 | 23 | Write |  |  |  |  | E
24 |  | g1130_PT_35301_BP_D | Turbine regulating oil pressure bypass from DCS | [7 empty] | D | 0 | 24 | Write |  |  |  |  | E
25 |  | g1130_PT_35501_BP_D | Turbine closing oil pressure bypass from DCS | [7 empty] | D | 0 | 25 | Write |  |  |  |  | E
26 |  | g1130_PT_35701_BP_D | Turbine exhaust pressure transmitter bypass from DCS | [7 empty] | D | 0 | 26 | Write |  |  |  |  | E
27 |  | g1130_PT_35702_BP_D | Turbine exhaust pressure transmitter bypass from DCS | [7 empty] | D | 0 | 27 | Write |  |  |  |  | E
28 |  | g1130_PT_35703_BP_D | Turbine exhaust pressure transmitter bypass from DCS | [7 empty] | D | 0 | 28 | Write |  |  |  |  | E
29 |  | g1130_SE_35503_BP_D | Turbine speed sensor BP from DCS | [7 empty] | D | 0 | 29 | Write |  |  |  |  | E
30 |  | g1130_SE_35504_BP_D | Turbine speed sensor BP from DCS | [7 empty] | D | 0 | 30 | Write |  |  |  |  | E
31 |  | g1130_SE_35505_BP_D | Turbine speed sensor BP from DCS | [7 empty] | D | 0 | 31 | Write |  |  |  |  | E
32 |  | g1130_TE_34701_BP_D | Compressor suction male rotor radial bearing temperature bypass from DCS | [7 empty] | D | 0 | 32 | Write |  |  |  |  | E
33 |  | g1130_TE_34702_BP_D | Compressor suction male rotor radial bearing temperature bypass from DCS | [7 empty] | D | 0 | 33 | Write |  |  |  |  | E
34 |  | g1130_TE_34703_BP_D | Compressor suction female rotor radial bearing temperature bypass from DCS | [7 empty] | D | 0 | 34 | Write |  |  |  |  | E
35 |  | g1130_TE_34704_BP_D | Compressor suction female rotor radial bearing temperature bypass from DCS | [7 empty] | D | 0 | 35 | Write |  |  |  |  | E
36 |  | g1130_TE_34705_BP_D | Compressor discharge male rotor radial bearing temperature bypass from DCS | [7 empty] | D | 0 | 36 | Write |  |  |  |  | E
37 |  | g1130_TE_34706_BP_D | Compressor discharge male rotor radial bearing temperature bypass from DCS | [7 empty] | D | 0 | 37 | Write |  |  |  |  | E
38 |  | g1130_TE_34707_BP_D | Compressor discharge female rotor radial bearing temperature bypass from DCS | [7 empty] | D | 0 | 38 | Write |  |  |  |  | E
39 |  | g1130_TE_34708_BP_D | Compressor discharge female rotor radial bearing temperature bypass from DCS | [7 empty] | D | 0 | 39 | Write |  |  |  |  | E
40 |  | g1130_TE_34709_BP_D | Compressor male rotor thrust bearing temperature bypass from DCS | [7 empty] | D | 0 | 40 | Write |  |  |  |  | E
41 |  | g1130_TE_34710_BP_D | Compressor male rotor thrust bearing temperature bypass from DCS | [7 empty] | D | 0 | 41 | Write |  |  |  |  | E
42 |  | g1130_TE_34711_BP_D | Compressor female rotor thrust bearing temperature bypass from DCS | [7 empty] | D | 0 | 42 | Write |  |  |  |  | E
43 |  | g1130_TE_34712_BP_D | Compressor female rotor thrust bearing temperature bypass from DCS | [7 empty] | D | 0 | 43 | Write |  |  |  |  | E
44 |  | g1130_TE_34713_BP_D | Gear box bearing temperature bypass from DCS | [7 empty] | D | 0 | 44 | Write |  |  |  |  | E
45 |  | g1130_TE_34714_BP_D | Gear box bearing temperature bypass from DCS | [7 empty] | D | 0 | 45 | Write |  |  |  |  | E
46 |  | g1130_TE_34715_BP_D | Gear box bearing temperature bypass from DCS | [7 empty] | D | 0 | 46 | Write |  |  |  |  | E
47 |  | g1130_TE_34716_BP_D | Gear box bearing temperature bypass from DCS | [7 empty] | D | 0 | 47 | Write |  |  |  |  | E
48 |  | g1130_TE_34717_BP_D | Gear box bearing temperature bypass from DCS | [7 empty] | D | 0 | 48 | Write |  |  |  |  | E
49 |  | g1130_TE_34718_BP_D | Gear box bearing temperature bypass from DCS | [7 empty] | D | 0 | 49 | Write |  |  |  |  | E
50 |  | g1130_TE_34719_BP_D | Gear box bearing temperature bypass from DCS | [7 empty] | D | 0 | 50 | Write |  |  |  |  | E
51 |  | g1130_TE_34720_BP_D | Gear box bearing temperature bypass from DCS | [7 empty] | D | 0 | 51 | Write |  |  |  |  | E
52 |  | g1130_TE_34721_BP_D | Turbine bearing temperature bypass from DCS | [7 empty] | D | 0 | 52 | Write |  |  |  |  | E
53 |  | g1130_TE_34722_BP_D | Turbine bearing temperature bypass from DCS | [7 empty] | D | 0 | 53 | Write |  |  |  |  | E
54 |  | g1130_TE_34723_BP_D | Turbine bearing temperature bypass from DCS | [7 empty] | D | 0 | 54 | Write |  |  |  |  | E
55 |  | g1130_TE_34724_BP_D | Turbine bearing temperature bypass from DCS | [7 empty] | D | 0 | 55 | Write |  |  |  |  | E
56 |  | g1130_TE_34725_BP_D | Turbine thrust bearing temperature bypass from DCS | [7 empty] | D | 0 | 56 | Write |  |  |  |  | E
57 |  | g1130_TE_34726_BP_D | Turbine thrust bearing temperature bypass from DCS | [7 empty] | D | 0 | 57 | Write |  |  |  |  | E
58 |  | g1130_TE_34727_BP_D | Turbine thrust bearing temperature bypass from DCS | [7 empty] | D | 0 | 58 | Write |  |  |  |  | E
59 |  | g1130_TE_34728_BP_D | Turbine thrust bearing temperature bypass from DCS | [7 empty] | D | 0 | 59 | Write |  |  |  |  | E
60 |  | g1130_TT_34101_BP_D | Compressor suction line temperature transmitter bypass from DCS | [7 empty] | D | 0 | 60 | Write |  |  |  |  | E
61 |  | g1130_TT_34102_BP_D | Compressor discharge line temperature transmitter bypass from DCS | [7 empty] | D | 0 | 61 | Write |  |  |  |  | E
62 |  | g1130_TT_34103_BP_D | Compressor discharge line temperature transmitter bypass from DCS | [7 empty] | D | 0 | 62 | Write |  |  |  |  | E
63 |  | g1130_TT_34104_BP_D | Compressor discharge line temperature transmitter bypass from DCS | [7 empty] | D | 0 | 63 | Write |  |  |  |  | E
64 |  | g1130_TT_34105_BP_D | Compressor discharge line temperature transmitter bypass from DCS | [7 empty] | D | 0 | 64 | Write |  |  |  |  | E
65 |  | g1130_TT_34301_BP_D | Lubricating oil tank temperature transmitter bypass from DCS | [7 empty] | D | 0 | 65 | Write |  |  |  |  | E
66 |  | g1130_TT_34302_BP_D | Lubricating oil supply manifold temperature transmitter bypass from DCS | [7 empty] | D | 0 | 66 | Write |  |  |  |  | E
67 |  | g1130_VE_34901_BP_D | Compressor bearing vibration bypass from DCS | [7 empty] | D | 0 | 67 | Write |  |  |  |  | E
68 |  | g1130_VE_34902_BP_D | Compressor bearing vibration bypass from DCS | [7 empty] | D | 0 | 68 | Write |  |  |  |  | E
69 |  | g1130_VE_34903_BP_D | Compressor bearing vibration bypass from DCS | [7 empty] | D | 0 | 69 | Write |  |  |  |  | E
70 |  | g1130_VE_34904_BP_D | Compressor bearing vibration bypass from DCS | [7 empty] | D | 0 | 70 | Write |  |  |  |  | E
71 |  | g1130_VE_34905_BP_D | Compressor bearing vibration bypass from DCS | [7 empty] | D | 0 | 71 | Write |  |  |  |  | E
72 |  | g1130_VE_34906_BP_D | Compressor bearing vibration bypass from DCS | [7 empty] | D | 0 | 72 | Write |  |  |  |  | E
73 |  | g1130_VE_34907_BP_D | Compressor bearing vibration bypass from DCS | [7 empty] | D | 0 | 73 | Write |  |  |  |  | E
74 |  | g1130_VE_34908_BP_D | Compressor bearing vibration bypass from DCS | [7 empty] | D | 0 | 74 | Write |  |  |  |  | E
75 |  | g1130_VE_34909_BP_D | Gear box bearing vibration bypass from DCS | [7 empty] | D | 0 | 75 | Write |  |  |  |  | E
76 |  | g1130_VE_34910_BP_D | Gear box bearing vibration bypass from DCS | [7 empty] | D | 0 | 76 | Write |  |  |  |  | E
77 |  | g1130_VE_34911_BP_D | Gear box bearing vibration bypass from DCS | [7 empty] | D | 0 | 77 | Write |  |  |  |  | E
78 |  | g1130_VE_34912_BP_D | Gear box bearing vibration bypass from DCS | [7 empty] | D | 0 | 78 | Write |  |  |  |  | E
79 |  | g1130_VE_34913_BP_D | Gear box bearing vibration bypass from DCS | [7 empty] | D | 0 | 79 | Write |  |  |  |  | E
80 |  | g1130_VE_34914_BP_D | Gear box bearing vibration bypass from DCS | [7 empty] | D | 0 | 80 | Write |  |  |  |  | E
81 |  | g1130_VE_34915_BP_D | Gear box bearing vibration bypass from DCS | [7 empty] | D | 0 | 81 | Write |  |  |  |  | E
82 |  | g1130_VE_34916_BP_D | Gear box bearing vibration bypass from DCS | [7 empty] | D | 0 | 82 | Write |  |  |  |  | E
83 |  | g1130_VE_34917_BP_D | Turbine bearing vibration bypass from DCS | [7 empty] | D | 0 | 83 | Write |  |  |  |  | E
84 |  | g1130_VE_34918_BP_D | Turbine bearing vibration bypass from DCS | [7 empty] | D | 0 | 84 | Write |  |  |  |  | E
85 |  | g1130_VE_34919_BP_D | Turbine bearing vibration bypass from DCS | [7 empty] | D | 0 | 85 | Write |  |  |  |  | E
86 |  | g1130_VE_34920_BP_D | Turbine bearing vibration bypass from DCS | [7 empty] | D | 0 | 86 | Write |  |  |  |  | E
87 |  | g1130_ZE_34901_BP_D | Compressor thrust bearing displacement bypass from DCS | [7 empty] | D | 0 | 87 | Write |  |  |  |  | E
88 |  | g1130_ZE_34902_BP_D | Compressor thrust bearing displacement bypass from DCS | [7 empty] | D | 0 | 88 | Write |  |  |  |  | E
89 |  | g1130_ZE_34903_BP_D | Compressor thrust bearing displacement bypass from DCS | [7 empty] | D | 0 | 89 | Write |  |  |  |  | E
90 |  | g1130_ZE_34904_BP_D | Compressor thrust bearing displacement bypass from DCS | [7 empty] | D | 0 | 90 | Write |  |  |  |  | E
91 |  | g1130_ZE_34905_BP_D | Turbine displacement bypass from DCS | [7 empty] | D | 0 | 91 | Write |  |  |  |  | E
92 |  | g1130_ZE_34906_BP_D | Turbine displacement bypass from DCS | [7 empty] | D | 0 | 92 | Write |  |  |  |  | E
93 |  | gFlow1_AM_1A1_D | PID manual auto from DCS | [7 empty] | D | 0 | 93 | Write |  |  |  |  | O
94 |  | gHD2_1A1_D | Governor-HMI raise button from DCS | [7 empty] | I | 0 | 94 | Write |  |  |  |  | O
95 |  | gHD3_1A1_D | Governor-HMI lower button from DCS | [7 empty] | I | 0 | 95 | Write |  |  |  |  | O
96 |  | gLAMP_TEST_1A1_D | lamp test from DCS | [7 empty] | I | 0 | 96 | Write |  |  |  |  | O
97 |  | gLP1_ST_1A1_D | 1# lubricating oil pump start from DCS | [7 empty] | I | 0 | 97 | Write |  |  |  |  | O
98 |  | gLP2_ST_1A1_D | 2# lubricating oil pump start from DCS | [7 empty] | I | 0 | 98 | Write |  |  |  |  | O
99 |  | gNORM_STP_1A1_D | Governor- normal stop(HMI) from DCS | [7 empty] | I | 0 | 99 | Write |  |  |  |  | O
100 |  | gPress1_AM_1A1_D | PID manual auto from DCS | [7 empty] | D | 0 | 100 | Write |  |  |  |  | O
101 |  | gRESET_TRIP_1A1_D | Reset from DCS | [7 empty] | I | 0 | 101 | Write |  |  |  |  | O
102 |  | gSA_1A1_D | GOVERNOR-REMOTE/LOCAL SELECTOR from DCS | [7 empty] | D | 0 | 102 | Write |  |  |  |  | O
103 |  | gSTART_1A1_D | Governor-Start(HMI) from DCS | [7 empty] | I | 0 | 103 | Write |  |  |  |  | O
104 |  | gSTART_AM_1A1_D | Governor-1= auto raise 0=manual raise from DCS | [7 empty] | D | 0 | 104 | Write |  |  |  |  | O
105 |  | gTemp1_AM_1A1_D | PID manual auto from DCS | [7 empty] | D | 0 | 105 | Write |  |  |  |  | O
106 |  | gWM1_C_H_1A1_D | Governor-1= warm state 0= cold state from DCS | [7 empty] | D | 0 | 106 | Write |  |  |  |  | O

## NOTE
№ п/п | Date / Дата | Type of check / Тип проверки | Identified comments / Выявленные замечания | Responsible / Ответственные | Notes / Примечания | Status / Статус | Reply 20260316
1 | 2026-01-27 | Software | Add interlock indication on each "interlock"graphic jumper to indicate there're interlock conditions. Добавить индикацию наличия сработанной блокировки на каждой кнопке "Interlock" | Consen |  | Close / Закрыто
3 | 2026-01-27 | Documentation | The documents NKNH21002-1133-PO0008-112-0031 "Cause & Effect Diagrams Off Gas Compressor 1130-K-301A," NKNH21002-1133-PO0008-112-0032 "Cause & Effect Diagrams Off Gas Compressor 1130-K-301B" correct in accordance with the design documentation of the turbine supplier and directed comments Документы NKNH21002-1133-PO0008-112-0031 "Cause & Effect Diagrams Off Gas Compressor 1130-K-301A", NKNH21002-1133-PO0008-112-0032 "Cause & Effect Diagrams Off Gas Compressor 1130-K-301B" откорректировать в соответствии с проектной документацией поставщика турбины и направленным замечаниям | DaLong/SSEC | DaLong will provide modified documentation to SSEC and Sibur. DaLong предоставит измененную документацию в SSEC и Сибур | Open / Открыто
4 | 2026-01-27 | Software | Add the logic of automatic determination of compressor state (hot/cold). "Warm/cold " switch must be available on the screen only at "Manual" control mode and Mode 0, Mode 1, Mode 2 Реализовать логику автоматического определения состояния компрессора (горячий/холодный). Ключ "горячий/холодный режим" должен быть доступен на экране только при режиме управления "Ручной" и режимах пуска Mode 0, Mode 1, Mode 2 | Consen |  | Close / Закрыто
5 | 2026-01-28 | Software | automatic lub oil logic needs to be modified Automatic control logic of lube oil pumps needs to be modified (AND element to be replaced with OR Логика автоматического управления смазочными насосами должна быть откорректирована (элемент AND должен быть заменен на OR) | Consen | Sibur confirms the start signal is pulse signal. Сибур подтвердил, сигнал на запуск насосов импульсный | Close / Закрыто
6 | 2026-01-28 | Software | For the logic of the permission to start of the lube oil pumps, add the "1of2" condition of the speed sensors 1330-SI-35501/35502 Для логики разерешния пуска смазочных насосов реализовать условие "1из2" датчиков скорости 1330-SI-35501/35502 | DaLong/Consen |  | Close / Закрыто
7 | 2026-01-28 | Software | 1130-FI-34101 incorrect flow rate calculation, correct 1130-FI-34101 неверное вычисление расхода, исправить | Consen |  | Close / Закрыто
8 | 2026-01-28 | Software | Make FV34101 FO symbol bigger. Мнемознак клапана 1130-TV-34101 увеличить | Consen |  | Close / Закрыто
9 | 2026-01-28 | Software | add lub oil pump logic on HMI (new screen). Добавить логику управления смазочных насосов на HMI (новый кадр) | Consen |  | Close / Закрыто
10 | 2026-01-28 | Software | Mode 0 Trip color change to red,and Mode 1 color change to yellow. Мнемознак состояния "Mode 0" (активная блокировка) должен быть красный, "Mode 1" желтый | Consen |  | Close / Закрыто
11 | 2026-01-28 | Software | 1130-PT-35501 tag number is incorrect on HMI 1130-PT-35501 исправить тэг на HMI | Consen |  | Close / Закрыто
12 | 2026-01-28 | Software | On windows "Real-time alarms", "History alarms", "Events" comments is empty. В окнах "Real-time alarms", "History alarms", "Events" отсутствует описание | Consen |  | Close / Закрыто
13 | 2026-01-28 | Software | History curve print should have unit and legend На выгрузках трендов добаить легенду и единицы измерения. | Consen |  | Open / Открыто
14 | 2026-01-28 | Documentation | add user management (including acess level)chapter in system description file В документ "Описание системы управления" добавить описание управления доступом | Consen | Consen will provide this documentation to SSEC and Sibur Consen предоставит данную документацию SSEC и Сибуру | Open / Открыто
15 | 2026-01-28 | Software | Sibur request add MOS enable switch on auxilary console in CCR in order to enable ITCC MOS permission. Добавить сигнал "MOS разрешен" c переключателя на ESD панели | DaLong/SSEC/Consen | DaLong need confirm this solution with SSEC DaLong необходимо подтвердить это решение с SSEC | Open / Открыто | SSEC: will add MOS enable switch on auxilary console.
16 | 2026-01-29 | Software | Normal MOS operation process will be: step 1:MOS enable switch on auxilary console to enable. step 2: MOS bypass switch on DCS software switch to bypass. step 3: after maintainance work finish, MOS bypass switch on DCS sotware switch to normal. step 4: MOS enable switch on auxilary console switch to disable. Note: Signals in 1 SIF loop can only be bypassed at most 1,and this should be done in DCS. bypass timeout function is not required. Нормальный процесс эксплуатации MOS: шаг 1:Переключатель "MOS разрешен" на панеди ESD переводится в состояние ВКЛ. шаг 2: На экране оператора DCS для отдельного сигнала включается режим MOS. шаг 3: После окончания работ по техническому обслуживанию, для сигнала режим MOS выключается. шаг 4: Переключатель "MOS разрешен" на панеди ESD переводится в состояние ВЫКЛ. Примечание.Сигналы в 1 контуре SIF могут быть обойдены только максимум 1, и это должно быть сделано в РСУ. функция времени ожидания обхода не требуется. | Dalong/SSEC/Consen | DaLong need confirm this solution with SSEC DaLong необходимо подтвердить это решение с SSEC | Open / Открыто | SSEC: confirmed.
17 | 2026-01-29 | Software | Sibur request add commssioning mode only in program and not on HMI. When this mode is on, ITCC will have full control authorization without the restriction of MOS algorithm. When this mode is off, DCS will have full control authorization, and normal MOS operation process should be followed. Добавить режим "ПНР" в проекте PLC без вывода на верхний уровень. Когда этот режим включен, ITCC будет иметь полную авторизацию управления без ограничения алгоритма MOS. Когда этот режим выключен, РСУ будет иметь полную авторизацию управления, и должен соблюдаться нормальный процесс эксплуатации MOS. | DaLong/Consen/Sibur |  | Close / Закрыто | SSEC: confirmed.
18 | 2026-01-29 | HMI | Translate all text, including units of measurement into Russian Перевести весь текст, ключая единицы измерения на русский язык | DaLong/Consen |  | Open / Открыто
19 | 2026-01-29 | HMI | Implement a request to accept a switch with confirmation from the operator to exclude accidental clicks. Добавить двойное подтверждение на дейсвтия оператора | Consen |  | Close / Закрыто
20 | 2026-01-29 | HMI | Наименование тегов привести в соответствие с P&ID. Структура тега должна быть 1130-ХХ-ХХХХХ. По датчикам и исполнительным механизмам. Name of tags to match with P&ID. The tag structure must be 1130-ХХ-ХХХХХ. By sensors and actuators. | Consen |  | Close / Закрыто
21 | 2026-01-29 | HMI | No speed units specified on screens "Interlock7", "Turbine process" Не указаны единицы измерения скорости на мнемосхема "Interlock7", "Turbine process" | Consen |  | Close / Закрыто
22 | 2026-01-29 | HMI | Specify the OR logic unit in accordance with GOST on screen "Permissive". Replace with 1 Блок логики OR указать в соответствии с ГОСТ на экране "Permissive". Заменить на 1 | Consen |  | Close / Закрыто
23 | 2026-01-29 | HMI | Remove the 1130-TI-34102 on the water line downstream of the compressor and indicate the 1130-TIC-34102 instead. Information uplift. Убрать 1130-TI-34102 на линии воды после компрессора и вместо него указать 1130-TIC-34102. Задвоение информации. | Consen |  | Close / Закрыто
24 | 2026-01-29 | HMI | The on-off shut-off valves shall be marked with a status symbol (open/closed) in addition to the color symbol. По запорным двухпозиционным клапанам должна появлятся буква с обозначением состояние (открыт/закрыт) в дополнение к цветовому обозначению. | Consen |  | Close / Закрыто
25 | 2026-01-29 | HMI | No Water Control Valve, Main stop valve, Steam inlet control valve, Valve Nitrogen Seal Tags Отсутствует позиционное обозначение клапанов Water Control Valve, Main stop valve, Steam inlet control valve, Valve Nitrogen Seal | Consen |  | Close / Закрыто
26 | 2026-01-29 | HMI | Units are not specified 1130-KI-34901 Не указаны единицы измерения 1130-KI-34901 | Consen |  | Close / Закрыто
27 | 2026-01-29 | HMI | Add a column with readings in mA for AI and AO to the Signal list mnemonic diagram (required for calibration and verification) Добавить на мнемосхему "Signal list" столбец с показаниями в мА для AI и AO (требуется для калибровки и сдачи в поверку) | Consen | Consen will modify. Consen внесет изменения | Open / Открыто
28 | 2026-01-29 | HMI | Add "Alarm and Lock" mimics Добавить окно "Сигнализация и блокировки" | Consen | Consen will modify. Consen внесет изменения | Open / Открыто
29 | 2026-01-30 | Software | Include FAULT signals in activing ITCC alarm signals to ESD. В логику срабатывания дискретного сигнала "Неисправность ITCC" добавить несиправности аналоговых сигналов | Consen |  | Close / Закрыто
30 | 2026-01-30 | Hardware | In the drawing "NKNH21002-005-ATX.DW-7004", the CCS workstation is in CCR, and there's one remote cabinet is in Rack room. But now no computer in CCR and no cabinet in Rack room. Which solution should be used? На чертеже «NKNH21002-005-ATX.DW-7004,» рабочая станция CCS (ITCC) и удаленный шкаф располагаются в операторной. Но согласно документации Dalong и Consen все оборудование располагается в FAR. Какое решение следует использовать? | SSEC | SSEC reply that no computer in CCR and no remote cabinet in Rack room,and 2 computers in FAR. SSEC should modify “NKNH21002-005-ATX.DW-7004” SSEC ответил, что в CCR не будут располагаться рабочая станция и удаленный шкаф | Open / Открыто | SSEC： No computer in CCR, and DCS control ITCC equimpment though modbus TCP. the drawing "NKNH21002-005-ATX.DW-7004" shall be modified.
31 | 2026-01-30 | Hardware | Provide complete equipment specification with prices for 2-year spare parts list and commissioning spares parts list Предоставить полную спецификацию оборудования с ценами для формирования перечня запасных частей на 2 года и запасных частей для пусконаладки | Dalong/Sibur | Sibur will send spares requirement for 2-year operation to SSEC Сибур направит требование по запасным частям на 2 годаэксплуатации в SSEC | Open / Открыто
32 | 2026-01-30 | Hardware | Provided Commissioning Spare Parts Pen does not meet Sibur requirements Предоставленный перечень запасных частей для пусконаладки не удовлетворяет требованиям Сибура | SSEC/Dalong/Sibur | Sibur will send spares requirement for commissioning to SSEC Сибур направит требование по запасным частям к пусконаладки в SSEC | Open / Открыто
33 | 2026-01-30 | Software/DCS communication | add one HMI/DCS control switch on HMI, when switch this key to DCS control, DCS will have full control, and when switch this key to HMI control, HMI will have full control. DCS can't operate this switch but need to indicate the status. DCS can't operate overspeed test switch but need to indicate the status. when in DCS control mode, overspeed test button can't be operated on HMI. Добавить один переключатель управления HMI/DCS на HMI, при переключении этого ключа на управление РСУ, РСУ будет иметь полный контроль, а при переключении этого ключа на управление HMI, HMI будет иметь полный контроль. DCS не может управлять этим переключателем, но должна выводить на экран его состояние. РСУ не может управлять переключателем проверки защиты сверхоборотов, но должна выводить на экран его состояние. в режиме управления РСУ кнопка контроля превышения скорости не может работать на HMI. | Dalong/Consen/SSEC | DaLong needs to confirm this solution with SSEC.Consen will modify. DaLong должен подтвердить это решение с SSEC.Consen изменит. | Open / Открыто | SSEC：confirmed.
34 | 2026-01-30 | Documentation | Consen will describe operation control description on HMI and DCS, and DaLong will add DCS operation control descreption on compressor manual. Consen опишет описание управления работой в HMI и РСУ, а DaLong добавит описание управления работой с РСУ и HMI в руководство по эксплуатации компрессора. | Consen/DaLong | after SSEC confirm, Consen and Dalong will provide this manual. После подтверждения от SSEC Consen и DaLong внесут изменения в документацию | Open / Открыто
35 | 2026-01-30 | Software/DCS communication | the signals don't send to DCS are as below: HMI_stop,overspeed test switch. сигналы, которые не передаются в РСУ, перечислены ниже: HMI_stop,overspeed test switch. | Consen | DaLong needs to confirm this solution with SSEC.Consen will modify. DaLong должен подтвердить это решение с SSEC.Consen изменит. | Open / Открыто | SSEC：confirmed.
36 | 2026-01-30 | Software/DCS communication | no matter what's the DCS_HMI_control_switch status, the signals should always work are as below: HMI_stop независимо от статуса DCS_HMI_control_switch, сигналы всегда должны работать следующим образом: HMI_stop | Consen | DaLong needs to confirm this solution with SSEC.Consen will modify. DaLong должен подтвердить это решение с SSEC.Consen изменит. | Open / Открыто | SSEC：confirmed.
37 | 2026-01-30 | Software/DCS communication | Add one heartbeat signal send from ITCC to DCS. ITCC generate a 5 seconds duration true signal every 10 seconds. DCS check if they can receive the true signal every 10 seconds. If can't, DCS should generate communication lost alarm. Добавить сигнал проверки наличия связи, передаваемого из ITCC в DCS. ITCC генерирует истинный сигнал продолжительностью 5 секунд каждые 10 секунд. DCS проверяет возможность получения истинного сигнала каждые 10 секунд. В противном случае РСУ должна генерировать аварийный сигнал потери связи. | Consen/SSEC | DaLong needs to confirm this solution with SSEC.Consen will modify. DaLong должен подтвердить это решение с SSEC.Consen изменит. | Open / Открыто | SSEC：confirmed.
38 | 2026-01-30 | DCS communication | modbus mapping list should be updated to include DCS commands to ITCC,including changing values, operating equimpment.Consen send mapping list and screenshots of HMI to Dalong, Dalong send to SSEC, SSEC send to DCS Vendor (Tecon). Карта modbus адрессов должна быть обновлена в части включения команд РСУ в ITCC, включая команды урпавления оборудованием. Consen должен предоставить карту modbus адрессов и экраны HMI в Dalong, Dalong - в SSEC, SSEC - поставщику РСУ (Tecon). | Consen/DaLong/SSEC | DaLong needs to confirm this solution with SSEC.Consen will provide. DaLong должен подтвердить это решение с SSEC.Consen предоставит. | Open / Открыто | SSEC:confirmed.